## Overview
SLAM Assets
Generated on | March 24, 2026
Generated for | SLAM
Generated by | Bill Roth
Status | Active

## Data
Flags | Asset ID | Facility No | Asset Name | Description | Address | City | Province / State | Postal / ZIP | Full Condition Assessment Date | Assessment Year | Year Constructed | Effective Age | Element Count | Recommendation Count | Replacement Value | Overall Narrative | Architectural Narrative | Mechanical Narrative | Electrical Narrative | Site Narrative | Area (sq m) | Converted Area (sq ft) | GFA Footprint | Floors | Basement Levels | Regional Factor | Ownership Type | Historical | Use | Comments | 3 Year Rec Costs | 3 Year FCI | 5 Year Rec Costs | 5 Year FCI | A) Parking: Are accessible parking spaces, access aisles, and signage provided in required locations and quantities, and do they meet level and proximity requirements for accessibility? | B) Exterior Accessible Routes: Is there a continuous, unobstructed, and properly sloped accessible route from public transportation and sidewalks to building entrances? | C) Interior Accessible Routes: Are all building entrances, routes, doors, vestibules, and elevators sufficiently accessible, clearly identified, and equipped with compliant hardware, signage, and controls throughout public areas? | D) Toilet Rooms: Are toilet rooms and fixtures: lavatories, stalls, urinals, and grab bars provided and arranged to meet accessibility standards for space, height, fixtures, and protection? | Asset Type | Campus | Zone
| 5 | 01.053 | Bespin Auditorium | A historic, grand performance hall hosting concerts, lectures, and university ceremonies. It is known for its impressive architecture and large audience capacity. | 205 20th St | Brandon |  |  | 2023-11-05 | 2023 | 1928 | 97 | 94 | 85 | 90064655.35 | This centre consists of a main one-storey structure with an additional single-storey extension. The layout incorporates classrooms, workshop spaces, storage rooms, and utility areas. The design serves both instructional and practical training functions within the facility. | General: Bespin Auditorium was constructed in 1928 and is located at 205 20th St. Based on the provided information, the total gross floor area is estimated to be approximately 23,276 square meters. The building was assessed Nov 5, 2019. The building mainly consists of offices and labs. Structural Summary: Bespin Auditorium is a three-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is a concrete infilled metal pan deck on open web steel joists. Envelope Summary: The exterior walls is split face concrete masonry and precast panels. The exterior windows are aluminum-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The building's roof is an inverted roof assembly where the roof membrane is a single-ply built-up roof membrane. Interior Summary: The floor finishes of the building interior consists of carpet tiles, painted floor finish and vinyl tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include gypsum board ceiling finish, eggcrate tiles and acoustic ceiling tiles. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Ventilation for the building is provided from an air handling unit located in Block G. Space heating is provided is provided by electric baseboard heaters with a unit heater in the rock storage area. Exhaust fans are provided for general building and washroom exhaust. A newer DDC system and an older hybrid DDC/pneumatic system is utilized for control of the HVAC system. Conveying equipment for the building consists of a three storey passenger elevator. | Electrical power is provided from the CUB to 600V – 120/208V step-down transformers and includes incoming feeders; as well as panelboards and motor control centres. Interior lighting for the building consists of surface mounted light fixtures with T8 lamps and electronic ballasts, conduit and wire. Exterior lighting consists of HID surface mounted units. | Landscaped terraces and wide walkways accommodate event crowds, with benches and flagpoles enhancing the site. Drop-off and accessible parking zones are provided. Lighting and signage aid in visitor orientation. | 23276 | 250541 |  | 3 |  | 1 | owned | N | Assembly (Auditorium, Theater) |  | 38354170.93 | 42.6% | 39779069.55 | 44.2% | Yes – Signage directs to accessible parking without obstruction. | Yes – Public transaction counters are accessible and at a compliant height. | Yes – Ramps have compliant handrails, slopes, and landings. | Yes – Accessible toilet rooms are clearly identified with signage. | Academic | Brandon Campus West | South
| 1 | 04.758 | Humanities Fine Arts | A multi-purpose academic building housing classrooms, offices, and studios for visual arts, music, theatre, and humanities departments. It typically includes performance spaces, art galleries, and rehearsal rooms. | 6265 Crescent Road | Vancouver |  |  | 2023-10-15 | 2023 | 1971 | 54 | 141 | 126 | 15576550.93 | This gallery consists of a three-story structure with a basement, featuring extensive renovations and the addition of stairwells at both its north and south ends. The facility houses a range of functions: office spaces predominantly on the upper level, multiple gallery rooms, storage areas, a gift shop, studio, lecture hall, kitchen, and custodial rooms, in addition to mechanical and electrical service areas. A designated shipping and receiving section is situated at the south end of the building. | General: Humanities Fine Arts was constructed in 1971 and is located at 6265 Crescent Road. Based on the provided information, the total gross floor area is estimated to be approximately 10,179 square meters. The building was assessed on Oct 15, 2019. The building is mainly used for educational purposes. Structural Summary: A Building is a five-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is of reinforced concrete supported by concrete beams and columns. Envelope Summary: The exterior walls are stone cladding and curtain walls. The exterior windows are metal-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The flat roof structure has a conventional roof assembly system, where the roof membrane is a multi-ply built-up roof membrane protected by a white flood coat and white aggregate surfacing system. Interior Summary: The floor finishes of the building interior consists of vinyl floor tiles, sheet vinyl, urethane floor, painted concrete floors and porcelain tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include bamboo panel ceiling, epoxy painted ceiling, metal panel ceiling, and painted ceiling finish. Individual washrooms are provided in the building. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Domestic hot water is provided from domestic hot water tank heaters. Ventilation with heating and cooling for the building is provided from air handling units. Heating medium is provided from hot water boilers. Heating in public spaces is provided by hot water baseboard, fin tube, wall convectors and force flow heaters. Cooling medium is provided from chillers and cooling towers. Cooling for some spaces is provided from rooftop evaporative coolers and DX units. Rooftop exhaust fans are provided for general building and washroom exhaust. A DDC system is utilized for control of the HVAC system. Conveying equipment for the building consists of three passenger elevators. | Electrical power is provided from the CUP to a 3000A, 600V, 3-Phase, 4-Wire, SQUARE D, Main Breaker Distribution Switchboard that includes incoming feeder, distribution breakers, distribution feeders and metering; as well as distribution switchboards, panelboards and motor control centres. Interior lighting for the building consists of surface mounted and recessed light fixtures with T5 lamps and electronic ballasts as well as pendant type fixtures with compact fluorescent lamps, conduit and wire. Exterior lighting consists of LED surface mounted and recessed units. | Landscaping features ornamental plantings and art display areas with concrete walkways connecting main entrances to campus paths. Benches and bicycle racks are provided near primary entrances. Site lighting ensures visibility for evening access. | 10179 | 109566 |  | 5 |  | 1.25 | owned | N | Academic |  | 5193991.6 | 33.3% | 6968579.37 | 44.7% | Yes – Sufficient accessible spaces, aisles, and signage are present and compliant. | Yes – Route from public transport and sidewalks is unobstructed and properly sloped. | Yes – Entrances, doors, and elevators are accessible and clearly identified. | Yes – Toilet rooms and fixtures are all ADA compliant in layout and equipment. | Academic | Main Campus | Central
| 2 | 03.523 | Kamino Student Ctr | A central student union building with lounges, dining options, meeting rooms, and event spaces. It serves as a hub for student activities, organizations, and campus services. | 149 Smallwood Drive | Mount Pearl |  |  | 2023-11-07 | 2023 | 1954 | 71 | 59 | 56 | 11150650.2 | This centre features a substantial footprint and is designed to support varsity sports and related activities, incorporating two ice rinks, team rooms, administrative offices, corridors, food service areas including a kitchen and cafeteria, as well as multiple storage and mechanical rooms. The facility is organized to provide comprehensive support for sporting events, training, and daily operations. | General: Kamino Student Ctr was constructed in 1954 and is located at 149 Smallwood Drive. Based on the provided information, the total gross floor area is estimated to be approximately 10,890 square meters. The building was assessed Nov 7, 2019. The building mainly consists of offices and labs. Structural Summary: K Building is a three-story structure without a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is a concrete infilled metal pan deck on open web steel joists. Envelope Summary: The exterior walls is split face concrete masonry, insulated metal panels and precast panels. The exterior windows are aluminum-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The building's roof is an inverted roof assembly where the roof membrane is a single-ply built-up roof membrane. Interior Summary: The floor finishes of the building interior consists of carpet tile, painted floor finish and vinyl tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include gypsum board ceiling finish, and acoustic ceiling tiles. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Domestic hot water is provided from a domestic hot water tank heater. Ventilation with heating and cooling for the building is provided from an air handling unit. Heating medium is provided from the CUB. Heating in public spaces and mechanical rooms is provided by electric baseboard and hot water unit heaters. Cooling medium is provided from the CUB. Some rooms are provided with DX units. Rooftop exhaust fans are provided for general building and washroom exhaust. A hybrid DDC/pneumatic system is utilized for control of the HVAC system. | Electrical distribution consists of distribution switchboards, transformers and panelboards. Interior lighting for the building consists of surface and recessed mounted light fixtures with T8 lamps and electronic ballasts, conduit and wire. Exterior lighting consists of recessed mounted units with CF lamps. | The site includes plaza areas and landscaped courtyards, with paved pedestrian routes leading to entrances and nearby campus amenities. Bicycle parking and outdoor seating are situated near the building. Accessible parking and exterior lighting are provided. | 10890 | 117219 |  | 3 |  | 1.05 | owned | N | Academic / Administration |  | 6100082.97 | 54.7% | 6100082.97 | 54.7% | Yes – Access aisles are level and adjacent to accessible parking spaces. | Yes – Curb ramps are present where needed and meet slope requirements. | No – Elevator controls do not have braille/tactile indicators installed. | Yes – Lavatories, stalls, and urinals are at compliant heights with sufficient clearances. | Student Services | Central | Central
| 3 | 05.855 | Lando Gym | An athletics facility featuring a gymnasium for sports such as basketball and volleyball. It often includes fitness equipment, locker rooms, and spaces for classes or intramural activities. | 875 Morningside Ave | Toronto |  |  | 2023-11-08 | 2023 | 1976 | 49 | 82 | 78 | 22367286.48 | This one-storey academic and athletic facility includes classrooms, lecture halls, offices, dedicated study areas, a gymnasium, lounge spaces, storage rooms, and service zones such as utility and mechanical/electrical rooms. The design supports a variety of instructional, recreational, and administrative functions within a single structure. | General: Lando Gym was constructed in 1976 and is located at 875 Morningside Ave. Based on the provided information, the total gross floor area is estimated to be approximately 4,197 square meters. The building was assessed Nov 8, 2019. The building mainly consists of offices and labs. Structural Summary: H Building is a two-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is a concrete infilled metal pan deck on open web steel joists. Envelope Summary: The exterior walls is split face concrete masonry and precast panels. The exterior windows are aluminum-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The building's roof is an inverted roof assembly where the roof membrane is a single-ply built-up roof membrane. Interior Summary: The floor finishes of the building interior consists of sealed concrete, terrazzo floor finish and vinyl tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include gypsum board ceiling finish, eggcrate tiles and acoustic ceiling tiles. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Domestic hot water is provided from domestic hot water tank heaters. Ventilation for the building is provided from air handling units with heating and cooling coils which also serves Block D. Space heating is provided is provided by electric baseboard heaters with unit heaters in the loading dock and main electrical vault areas. Exhaust fans are provided for general building and washroom exhaust. A hybrid DDC/pneumatic system is utilized for control of the HVAC system. | Electrical power is provided from the CUP to a 2500 KVA, 13.8KV – 600V main transformer. Electrical distribution consists of a 3000A, 600V, 3-Phase, 4-Wire, Main Breaker Distribution Switchboard that includes incoming feeder, distribution breakers, distribution feeders and metering; as well as distribution switchboards, panelboards and a motor control centre. Interior lighting for the building consists of surface and recessed mounted light fixtures with T8 lamps and electronic ballasts, conduit and wire. Exterior lighting consists of recessed mounted units. | Athletic fields and open green spaces surround the gym, with paved walkways linking entrances to parking areas. Outdoor seating and fitness stations are available. Bike racks and service access are included. | 4197 | 45176 |  | 2 |  | 1.15 | leased | N | Athletic Facility / Gymnasium |  | 9298243.31 | 41.6% | 10270987.21 | 45.9% | Yes – Parking is located on the shortest accessible path to the entrance. | Yes – All accessible routes are unobstructed and lead to main entry points. | Yes – Hardware and door widths meet accessibility standards throughout. | Yes – Grab bars are properly located at each accessible stall. | Athletics | Northeast Campus | East
| 4 | 01.074 | Mayo Building | A large academic and research building, often associated with medical or health sciences programs. It includes lecture halls, labs, faculty offices, and sometimes specialized clinics. | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 91 | 89 | 29983284.84 | This centre is a six-story structure with a basement. The building features various spaces including classrooms, cafeterias, offices, a lobby, restaurant, storage areas, corridors, and mechanical service rooms. The facility is organized to accommodate a range of academic, administrative, dining, and support functions. | General: Mayo Building was constructed in 2007 and is located at 10365 97 Street NW. Based on the provided information, the total gross floor area is estimated to be approximately 80,162 square meters. The building was assessed Oct 16, 2019. The building is mainly used for educational purposes. Structural Summary: J Building is a five-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is precast slab supported by steel beams and columns. Envelope Summary: The exterior walls are stone cladding, copper cladding and curtain walls. The exterior windows are metal-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The flat roof structure has an inverted roof membrane assembly (IRMA) consisting of ballast, filter fabric, extruded polystyrene insulation board, drainage mat and a fully adhered single-ply membrane. Interior Summary: The floor finishes of the building interior consists of carpet tile, sheet vinyl, urethane floor, polished concrete floors and ceramic tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include painted ceiling finish and ACT ceiling finish. Individual washrooms are provided in the building. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Domestic hot water is provided from domestic hot water tank heaters. Ventilation with heating and cooling for the building is provided from air handling units. Heating medium is provided from hot water boilers. Heating in public spaces is provided by baseboard, fin tube and unit heaters. Cooling medium is provided from a chiller. Cooling for some spaces is provided from DX units. Rooftop exhaust fans are provided for general building and washroom exhaust. A DDC system is utilized for control of the HVAC system. Conveying equipment for the building consists of two passenger elevators. | Electrical power is provided from the CUP to a 1200A, 600V, 3-Phase, 4-Wire, CUTLER-HAMMER, Main Breaker Distribution Switchboard that includes incoming feeder, distribution breakers, distribution feeders and metering; as well as distribution switchboards and panelboards. Interior lighting for the building consists of surface mounted and recessed light fixtures with T5 lamps and electronic ballasts as well as pendant type fixtures with compact fluorescent lamps, conduit and wire. Exterior lighting consists of HID surface mounted units. | Formal entry plazas and shaded seating areas are linked by paved walkways. Parking is adjacent, and clear pedestrian routes connect to main entrances. Exterior lighting and wayfinding signage support site navigation. | 80162 | 862856 |  | 5 |  | 1 | owned | Y | Academic / Administration |  | 14274860.16 | 47.6% | 14344744.55 | 47.8% | Yes – Accessible parking stalls are marked with the International Symbol of Access. | Yes – The surface materials on exterior routes are smooth and non-slip. | Yes – All vestibules provide required maneuvering clearances. | Yes – Plumbing under lavatories is protected against contact. | Academic | East Campus | East
| 7 | 04.750 | Science | A general academic building for science departments such as biology, chemistry, and physics. It contains teaching labs, classrooms, faculty offices, and research facilities. | 60 9th Street | Hearst |  |  | 2023-11-07 | 2023 | 1965 | 60 | 66 | 64 | 106261797.45 | This science complex is a six-story structure. The facility features a range of spaces, including classrooms, laboratory areas, offices, greenhouse space, storage rooms, corridors, and mechanical support rooms. The design accommodates both instructional and research activities, providing comprehensive infrastructure for academic and scientific work. | General: Science Building was constructed in 1965 and is located at 60 9th Street. Based on the provided information, the total gross floor area is estimated to be approximately 13,812 square meters. The building was assessed Nov 7, 2019. The building mainly consists of offices and labs. Structural Summary: F Building is a two-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is a concrete infilled metal pan deck on open web steel joists. Envelope Summary: The exterior walls is split face concrete masonry and precast panels. The exterior windows are aluminum-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The building's roof is an inverted roof assembly where the roof membrane is a single-ply built-up roof membrane. Interior Summary: The floor finishes of the building interior consists of carpet tiles, epoxy finish, terrazzo floor finish and vinyl tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include gypsum board ceiling finish, eggcrate tiles and acoustic ceiling tiles. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Ventilation for the building is provided from air handling units which also serve Block B. Space heating is provided is provided by electric baseboard heaters. Exhaust fans are provided for general building and washroom exhaust. A hybrid DDC/pneumatic system is utilized for control of the HVAC system. | Electrical power is provided from the CUB to 600V – 120/208V step-down transformers and includes incoming feeders; as well as distribution switchboards, panelboards and motor control centres. Interior lighting for the building consists of surface mounted light fixtures with T8 lamps and electronic ballasts, conduit and wire. Exterior lighting consists of HID recessed units. | Native plantings frame pedestrian paths and outdoor study areas. Bike racks, recycling stations, and vehicle access serve building users. Walkways connect major building entrances with campus routes. | 13812 | 148671 |  | 2 |  | 1.25 | owned | N | Academic |  | 65496532.84 | 61.6% | 65496532.84 | 61.6% | Yes – Snow and debris are cleared promptly from accessible parking and routes. | Yes – Entry route from ride-hailing drop-off location is accessible and level. | Yes – All public interior paths are free from protruding objects or obstacles. | Yes – Mirrors in accessible restrooms are mounted at the proper height. | Academic | Hearst Campus | South
| 30 | 4.099 | Site Infrastructure |  | 60 9th Street | Hearst |  |  | 2023-11-07 | 2023 | 1965 | 60 | 0 | 0 | [5 empty] | Comprehensive site infrastructure encompasses all utilities, roads, paths, landscaping, and site systems. Components are integrated to support the operation and usability of campus facilities. Maintenance is ongoing to ensure functionality and safety. | 1 | 11 |  | 2 |  | 1.25 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Consolidated | Hearst Campus | South
| 26 | 1.915 | Site Services - Communications and Security |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Communication and security infrastructure includes underground and aboveground data cabling, surveillance cameras, and access control devices. Systems are routed through buildings and across campus. Coverage ensures building and site security. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 21 | 1.91 | Site Services - Cooling Distribution |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | This cooling distribution system features insulated steel piping that extends from a central utility building through underground tunnels to various service rooms. The infrastructure is designed to deliver chilled water or cooling services efficiently to multiple campus facilities. |  |  |  | Chilled water or cooling services are delivered by insulated pipes from the central plant through tunnels. Distribution reaches various service rooms. Infrastructure supports campus-wide cooling needs. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 24 | 1.913 | Site Services - Electrical Distribution |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | This electrical distribution system utilizes utility feeders to supply power to the campus. Distribution cables, including XLP or XLPE types, are installed both underground and aboveground, running through service tunnels to serve most buildings. Low-voltage branch wiring for panelboards, lighting, and receptacles is also provided both below and above ground throughout the site. |  |  |  | Electrical power is supplied by utility feeders, with distribution cables running aboveground and underground. Service tunnels route wiring to most buildings. Panelboards and lighting connections are distributed site-wide. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 22 | 1.911 | Site Services - Fuel Distribution |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | This fuel distribution system comprises underground natural gas piping, equipped with fittings and valves, designed to supply specific buildings across the site. The infrastructure ensures safe and reliable delivery of fuel to designated campus facilities. |  |  |  | Underground natural gas piping supplies fuel to campus facilities. Fittings and valves manage flow and control. Distribution supports building operations and heating. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 20 | 1.909 | Site Services - Heating Distribution |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | This heating distribution system consists of insulated steel piping equipped with valves and fittings, routed through underground tunnels to serve designated buildings. The infrastructure is designed to efficiently deliver heating services across multiple facilities on site. |  |  |  | Insulated piping in utility tunnels distributes heating to campus buildings. Valves and fittings provide control at key points. The system serves multiple facilities. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 16 | 1.905 | Site Services - Landscaping |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Landscaping consists of lawn areas, gardens, ornamental trees, and shrubs. Irrigation systems are installed where needed. Plantings frame entrances and pedestrian routes. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 27 | 1.916 | Site Services - Other Site Electrical Utilities |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Other electrical systems comprise emergency power, special controls, or distribution devices housed above or below grade. Infrastructure supports specific equipment and operational needs. Utilities extend to outbuildings and service areas. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 23 | 1.912 | Site Services - Other Site Mechanical Utilities |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | This site mechanical utilities system includes equipment such as exhaust fans, pumps, and unit heaters, all situated within service tunnels. These components support mechanical operations and environmental control across the campus infrastructure. |  |  |  | Mechanical services include exhaust fans, pumps, and unit heaters situated in service tunnels. These components support ventilation and climate control. Utilities extend to multiple campus buildings. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 29 | 1.918 | Site Services - Other Site Systems & Equipment |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Additional site systems include emergency call stations, weather monitoring equipment, and signage. Equipment is distributed throughout the campus for accessibility and safety. Installations are maintained for operational readiness. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 13 | 1.902 | Site Services - Parking Lots |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Parking areas paved with asphalt serve campus visitors, staff, and students. Accessible spaces, lighting, and marked pedestrian crossings are included. Landscaping buffers parking from adjacent sites. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 28 | 1.917 | Site Services - Pedestrian and Service Tunnels |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Underground tunnels provide protected routes for pedestrian circulation and service distribution. Access points connect major buildings. Tunnels also house mechanical and electrical utilities. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 12 | 1.901 | Site Services - Roads |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Internal roads surfaced with asphalt provide vehicular access throughout the campus. Clear signage identifies routes and intersections. Roadways are bordered by pedestrian walkways and landscaped verges. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 18 | 1.907 | Site Services - Sanitary Sewers |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | This sanitary sewer infrastructure consists of direct-buried piping, manholes, and cleanouts, designed to collect wastewater from campus buildings and convey it to the municipal combined sewer system. The system supports the efficient management and transport of sanitary flows across the site. |  |  |  | Underground piping with manholes and cleanouts collects wastewater from buildings. The system conveys flows to the municipal sewer. Components are located below grade. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 14 | 1.903 | Site Services - Sidewalks and Pathways |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Concrete and paved walkways connect buildings, parking, and site features. Paths are accessible and well-lit. Wayfinding signs guide pedestrian flow. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 15 | 1.904 | Site Services - Site Development |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 | [5 empty] | Site development includes grading, drainage systems, and utility servicing for buildings. Hardscapes and landscaped areas are integrated for functionality and appearance. Service areas are screened from public view. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 25 | 1.914 | Site Services - Site Lighting |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | This site lighting system features single, double, and triple armature light fixtures mounted on metal poles set on concrete pedestals. These are located across parking lots, roadways, walkways, and adjacent to various buildings. The fixtures include a combination of metal halide and newer LED units. Lighting for sports fields is provided by taller multi-armature poles equipped with HID fixtures. |  |  |  | Pole-mounted fixtures provide lighting for walkways, parking lots, roadways, and entrances. Both LED and traditional sources are present. Sports fields have dedicated high-mast lighting. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 19 | 1.908 | Site Services - Storm Sewers |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | This storm sewer system consists of underground piping, manholes, and catch basins, designed to collect and convey stormwater for discharge into the municipal system. The infrastructure is largely original to the site construction and is fully concealed below ground, limiting the ability to perform a comprehensive visual assessment. |  |  |  | Stormwater is managed through underground pipes, manholes, and catch basins. Runoff is conveyed to the municipal storm system. Infrastructure is mainly buried and not directly visible. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 17 | 1.906 | Site Services - Water Supply |  | 10365 97 Street NW | Edmonton |  |  | 2023-10-16 | 2023 | 2007 | 18 | 0 | 0 |  | The water supply system consists of direct-buried piping equipped with fittings and valves, facilitating the delivery of municipal water through tunnels to campus buildings. This infrastructure also includes distribution lines that serve multiple hydrant locations throughout the campus. |  |  |  | Municipal water is supplied to campus buildings via underground piping. Hydrants are distributed for fire protection. System includes main loops and branch lines. | 1 | 11 |  | 5 |  | 1 | owned | N | Utilities |  | 0 | 0.0% | 0 | 0.0% |  |  |  |  | Infrastructure - Breakout | East Campus | East
| 6 | 31.896 | Skytop Detector Building | A specialized research facility housing advanced scientific instrumentation for neutrino experiments. It is designed to support high-level particle physics research and data collection. | RR6 Achray Rd | Pembroke |  |  | 2023-11-04 | 2023 | 2011 | 14 | 65 | 62 | 90848194.98 | Skytop Detector Building was constructed in 2011 and is located at RR6 Achray Rd. Based on the provided information, the total gross floor area is estimated to be approximately 4,939 square meters. The building was assessed on Nov 4, 2019. The building is mainly used for educational purposes. | Skytop Detector Building is a two-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is a concrete infilled metal pan deck on open web steel joists. Envelope Summary: The exterior walls is split face concrete masonry. The exterior windows are aluminum-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The building's roof is an inverted roof assembly where the roof membrane is a single-ply built-up roof membrane. Interior Summary: The floor finishes of the building interior consists of carpet tiles, ceramic tiles, epoxy floor and vinyl tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include gypsum board ceiling finish and acoustic ceiling tiles. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Domestic hot water is provided from domestic hot water tank heaters. Ventilation with heating and cooling for the building is provided from air handling units. Heating medium is provided from the CUB. Heating in public spaces is provided by hot water baseboard, fin tube, heaters and fan coils in the vestibules. Cooling medium is provided from a chiller. Cooling for some spaces is provided from DX units. Exhaust fans are provided for general building and washroom exhaust. A DDC system is utilized for control of the HVAC system. Conveying equipment for the building consists of a three storey handicap lift. | Electrical power is provided from the CUP to a 300KVA, 600V – 120/208V, 3-Phase, transformer that includes incoming feeder. Electrical power distribution consists of panelboards distributed around the building. Interior lighting for the building consists of surface mounted light fixtures with T8 lamps and electronic ballasts, conduit and wire. Exterior lighting consists of LED surface mounted units. | Minimal landscaping with gravel or paved service roads provides access for operations. Security features include fencing and site lighting. Utility connections are oriented for functionality. | 4939 | 53163 |  | 2 |  | 1.18 | rented | N | Research |  | 51347370.03 | 56.5% | 51347370.03 | 56.5% | No – One van-accessible parking space is too narrow and needs remarking. | Yes – All route crossings have detectable warnings for visually impaired users. | Yes – Emergency call systems in elevators meet non-voice communication requirements. | Yes – Turning spaces in accessible stalls meet the minimum requirements. | Academic | Northeast Campus | East
| 8 | 03.521 | Sports and Health Ctr | A comprehensive facility for fitness, recreation, athletics, and sports-related health services. Amenities typically include gyms, courts, fitness studios, athletic training, and sometimes wellness clinics. | 68 Apex Rd | Toronto |  |  | 2023-11-07 | 2023 | 1953 | 72 | 72 | 66 | 174946775.29 | This athletics facility is composed of a main structure and two additions. The layout encompasses a variety of sports and fitness spaces, including gymnasiums, swimming pools, squash courts, arenas, changing rooms, offices, utility rooms, and mechanical areas. The design supports a wide range of recreational and competitive athletics, as well as associated administrative and support functions. | General: Sports and Health ctr was constructed in 1953 and is located at 68 Apex Rd. Based on the provided information, the total gross floor area is estimated to be approximately 23,924 square meters. The building was assessed Nov 7, 2019. The building mainly consists of offices and labs. Structural Summary: G Building is a two-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is a concrete infilled metal pan deck on open web steel joists. Envelope Summary: The exterior walls is split face concrete masonry and precast panels. The exterior windows are aluminum-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The building's roof is an inverted roof assembly where the roof membrane is a single-ply built-up roof membrane. Interior Summary: The floor finishes of the building interior consists of carpet tiles and vinyl tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include gypsum board ceiling finish, eggcrate tiles and acoustic ceiling tiles. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Ventilation for the building is provided from air handling units which also serve Block B. Space heating is provided is provided by electric baseboard heaters. Exhaust fans are provided for general building and washroom exhaust. A hybrid DDC/pneumatic system is utilized for control of the HVAC system. | Electrical power is provided from the CUB to 600V – 120/208V step-down transformers and includes incoming feeders; as well as distribution switchboards, panelboards and motor control centres. Interior lighting for the building consists of surface mounted light fixtures with T8 lamps and electronic ballasts, conduit and wire. Exterior lighting consists of HID recessed units. | Athletic fields and courts adjoin the facility, with walking and jogging paths across the site. Bleachers, bike racks, and marked parking areas support users. Drop-off and pedestrian access points are clearly defined. | 23924 | 257516 |  | 2 |  | 1.05 | owned | N | Multi-Use |  | 88118257.24 | 50.4% | 93701618.77 | 53.6% | Yes – Surface slopes in accessible parking areas are within required limits. | No – One exterior ramp exceeds the maximum allowable slope and requires correction. | Yes – Doors along accessible routes have appropriate signage and lever handles. | Yes – Paper towel dispensers and hand dryers are within accessible reach ranges. | Athletics | Downtown Campus | North
| 9 | 22.054 | The Mustafar Visitor Center | A welcoming facility for campus and garden visitors that features information services, exhibits, and amenities like a café and gift shop. It often serves as a starting point for tours and public programs. | 234 Donald Street | Winnipeg |  |  | 2023-11-06 | 2023 | 2003 | 22 | 73 | 68 | 295307213.59 | This single-storey facility features a crawl space. The building includes offices, a high bay garage, storage rooms, a kitchen, washrooms, utility spaces, and dedicated mechanical and electrical rooms. The interior layout is organized to support administrative, operational, and support functions within the structure. | General: The Mustafar Visitor Center was constructed in 2003 and is located at 234 Donald Street. Based on the provided information, the total gross floor area is estimated to be approximately 4,299 square meters. The building was assessed Nov 6, 2019. The building mainly consists of offices and labs. Structural Summary: D Building is a three-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is a concrete infilled metal pan deck on open web steel joists. Envelope Summary: The exterior walls is concrete masonry and precast panels. The exterior windows are aluminum-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The building's roof is an inverted roof assembly where the roof membrane is a single-ply built-up roof membrane. Interior Summary: The floor finishes of the building interior consists of carpet tiles, epoxy floor and vinyl tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include gypsum board ceiling finish, eggcrate tiles and acoustic ceiling tiles. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Domestic hot water is provided from domestic hot water tank heaters. Ventilation for the building is provided from an air handling unit located in Block F. Space heating is provided is provided by electric baseboard heaters. Exhaust fans are provided for general building and washroom exhaust. A hybrid DDC/pneumatic system is utilized for control of the HVAC system. Conveying equipment for the building consists of a three storey passenger elevator. | Electrical power distribution consists of panelboards which are distributed around the building. Interior lighting for the building consists of surface mounted light fixtures with T8 lamps and electronic ballasts, conduit and wire. Exterior lighting consists of surface mounted and recessed units. | Landscaped gardens and walking trails surround the building, with visitor parking and accessible paths leading to the entrance. Picnic areas and seating are integrated. Directional signage is present throughout. | 4299 | 46274 |  | 3 |  | 1.15 | owned | N | Recreation |  | 114669276.32 | 38.8% | 127084217.15 | 43.0% | Yes – All accessible parking spaces connect to accessible walkways. | Yes – Accessible routes remain usable during construction activities. | Yes – Directional signage assists users in navigating accessible routes inside. | Yes – All restrooms have sufficient transfer spaces next to toilets. | Administrative | West Campus | North
| 10 | 12.01 | University Teaching and Outreach Ctr | A building dedicated to faculty development, teaching innovation, and community engagement activities. It often houses workshops, training rooms, and offices for outreach programs. | 1155 Broadway E | Vancouver |  |  | 2023-11-06 | 2023 | 1991 | 34 | 77 | 68 | 539657253.11 | This learning centre is a one-story structure with a mechanical penthouse. The facility includes a large lecture hall with tiered seating, several interactive seminar rooms. a kitchen/servery, shipping and storage spaces, washroom facilities, workshop areas, classrooms, laboratory spaces, and a student lounge. The interior is designed to accommodate a variety of instructional, collaborative, and support functions. | General: University Teaching and Outreach ctr was constructed in 1991 and is located at 1155 Broadway E. Based on the provided information, the total gross floor area is estimated to be approximately 5,016 square meters. The building was assessed on Nov 6, 2019. The building mainly consists of offices and labs. Structural Summary: B Building is a three-story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. The floor construction is a concrete infilled metal pan deck on open web steel joists. Envelope Summary: The exterior walls is concrete masonry and precast panels. The exterior windows are aluminum-framed insulated glass units. Various types and shapes of exterior doors provide access to building. The building's roof is an inverted roof assembly where the roof membrane is a single-ply built-up roof membrane. Interior Summary: The floor finishes of the building interior consists of carpet tiles, epoxy floor and vinyl tiles. Interior partitions are painted gypsum board and painted concrete masonry. The ceiling finishes include gypsum board ceiling finish, egg crate tiles and acoustic ceiling tiles. | Plumbing for the building consists of domestic water, sanitary waste and rainwater drainage piping. Domestic hot water is provided from domestic hot water tank heaters. Ventilation is provided from air handling units located in Block E. Space heating is provided from electric baseboard heaters. Cooling for the fish lab is provided from a DX unit. Rooftop exhaust fans are provided for general building and washroom exhaust. A hybrid DDC/pneumatic system is utilized for control of the HVAC system. Conveying equipment for the building consists of a three storey passenger elevator. | Electrical power is provided from the CUP to a 1000A, 600V, 3-Phase, 4-Wire, Main Breaker Distribution Switchboard that includes incoming feeder, distribution breakers, distribution feeders and metering; as well as distribution switchboards and panelboards. Interior lighting for the building consists of surface mounted and recessed light fixtures with T8 lamps and electronic ballasts, conduit and wire. Exterior lighting consists of surface mounted and recessed units. | The site features landscaped frontages, concrete walkways connecting to adjacent buildings, and designated parking zones. Benches and bike racks are provided. Lighting and signage facilitate safe and easy access. | 5016 | 53992 |  | 3 |  | 1.15 | leased | N | Academic |  | 205512147.56 | 38.1% | 205512147.56 | 38.1% | Yes – Lighting in accessible parking areas is adequate for safety and navigation. | Yes – Exterior accessible routes connect main entrance and all key site features. | Yes – Accessible seating and clear routes are provided in all public spaces. | Yes – Toilet stall doors can be latched from the inside with one hand. | Administrative | Main Campus | West