## Overview
SLAM_Elements
Generated on | March 24, 2026
Generated for | SLAM
Generated by | Bill Roth
Asset | - All -
Uniformat Code | - All -
Condition | - All -
Status | Active

## Data
Flags | Facility # | Asset ID | Asset Name | City | Element ID | Element Descriptor | Uniformat Code | Uniformat Name | Description | Year Installed | Expected Useful Life | Expected Renewal Year | Observed Renewal Year | Last Assessment | Condition | Condition Narrative | Quantity | Units | Unit Cost | Soft Cost Factor | Regional Factor | Difficulty Factor | Element Cost | Recommendation Count | Element Status | Imported Element ID | Asset Type | Campus | Zone
| 01.053 | 5 | Bespin Auditorium | Brandon | 355 | Acid Proof Sheet Vinyl | C302021 | Rubber / Spring Gym Floor | The building's floor finishes include sheet vinyl located in rooms 212, 213, 220, 221 and 224. | 2014 | 20 | 2034 | 2034 | 2025-04-29 | 2 - Good | No deficiencies were observed or reported | 3993 | SM | 217.14 | 1.3 | 1 | 1 | 1127152.03 | 1 | Active | 1435 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 903 | Aluminum Sash | B202001 | Windows | The buildings exterior windows are aluminum framed with insulating glass. | 2024 | 35 | 2059 | 2058 |  | 1 - Very Good |  | 646 | SM | 1387.83 | 1.3 | 1 | 1 | 1165499.63 | 0 | Active |  | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 100 | Aluminum-Framed Single Doors | B203005 | Exterior - Hangar Doors | The exterior doors consist of glazed aluminum framed single-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 2012 | 25 | 2037 | 2037 | 2025-06-27 | 1 - Very Good | The exterior doors are in good condition overall, no major deficiencies were observed. | 5 | Lump Sum | 11288.2 | 1.3 | 1 | 1 | 73373.3 | 1 | Active | 1374 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 857 | Auto Transfer Switch | D509002 | Emergency Power Generator Systems - Up to 300kVA | The emergency power system for this building includes an auto transfer switch for the essential load. The ATS is located in the main electrical vault. | 2001 | 30 | 2031 | 2037 | 2025-06-29 | 1 - Very Good | No significant deficiencies were observed. | 104 | kVA | 589.4 | 1.3 | 1 | 1 | 79686.88 | 1 | Active | 1416 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 548 | Boiler HW - Gas-Fired - 2010 | D302002 | Hot Water Boilers - Up to 1000 MBH | Heating medium is provided from a Fulton gas-fired steam boiler rated at approximately 500 MBH. | 2010 | 30 | 2040 | 2040 | 2025-08-20 | 1 - Very Good | No significant deficiencies were observed. | 500 | MBH | 103.85 | 1.3 | 1 | 1 | 67502.5 | 1 | Active | 1438 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 337 | C302005 - Carpet | C302005 | Carpet Floor | Upgraded carpet and underpad installed - Second Phase in 2022 | 2022 | 10 | 2032 | 2035 | 2025-06-01 | 2 - Good |  | 9903 | SM | 103.85 | 1.3 | 1 | 1 | 1336954.52 | 1 | Active | 1465 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 343 | C302006 - Vinyl Sheet | C302006 | Masonry and Stone Floor | Vinyl Sheer | 2023 | 50 | 2073 | 2038 | 2025-08-04 | 1 - Very Good |  | 1100 | SM | 849.69 | 1.3 | 1 | 1 | 1215056.7 | 1 | Active | 1466 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 897 | Carpet Tile | C302005 | Carpet Floor | The building’s floor finishes include carpet tile floor finish located in the offices | 2025 | 10 | 2035 | 2034 |  | 1 - Very Good |  | 8724 | SM | 103.85 | 1.3 | 1 | 1 | 1177783.62 | 0 | Active |  | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 330 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet floor tiles located in the offices. | 2005 | 10 | 2015 | 2026 | 2024-07-15 | 4 - Poor | The carpet tiles are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 9731 | SM | 103.85 | 1.3 | 1 | 1 | 1313733.66 | 1 | Active | 1387 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 331 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the offices. | 2005 | 10 | 2015 | 2026 | 2024-08-03 | 4 - Poor | The carpet tiles are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 8396 | SM | 103.85 | 1.3 | 1 | 1 | 1133501.98 | 1 | Active | 1418 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 898 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tile flooring located in, conference rooms and miscellaneous spaces. | 2024 | 10 | 2034 | 2033 |  | 1 - Very Good |  | 9726 | SM | 103.85 | 1.3 | 1 | 1 | 1313058.63 | 0 | Active |  | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 607 | Central AHU - Air Handler - Heat Recovery Unit - HRU-1 - 25000 CFM | D304025 | Heat Exchangers - Plate and Frame | The HVAC system includes an ENG AIR, heat recovery unit (HRU-1) having a capacity of 2,5000 CFM. | 2007 | 30 | 2037 | 2032 | 2025-03-19 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 18625.53 | 1.3 | 1 | 1 | 24213.19 | 1 | Active | 1454 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 266 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish. The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 1994 | 25 | 2019 | 2035 | 2025-05-31 | 2 - Good | The washrooms are in fair condition overall, no significant deficiencies were observed. | 2 | Per Lavatory | 21334.7 | 1.3 | 1 | 1 | 55470.22 | 1 | Active | 1445 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 53 | Concrete Masonry Unit Exterior Walls | B201021 | Masonry | The building's exterior wall include sections of concrete masonry unit. | 1972 | 75 | 2047 | 2047 | 2025-11-07 | 1 - Very Good | The exterior wall is in good condition overall, no significant deficiencies were observed or reported. | 754 | SM | 726.96 | 1.3 | 1 | 1 | 712566.19 | 1 | Active | 1385 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 76 | Curtain Wall | B201030 | Curtain Walls / Window Walls | The building includes a curtain wall system located on the roof. | 1972 | 40 | 2012 | 2026 | 2024-08-17 | 4 - Poor | The curtain wall is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 560 | SM | 1538.89 | 1.3 | 1 | 1 | 1120311.92 | 1 | Active | 1460 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 75 | Curtain Walls | B201030 | Curtain Walls / Window Walls | The building includes a curtain wall system located on the roof. | 1972 | 40 | 2012 | 2026 | 2024-08-15 | 4 - Poor | The curtain walls are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 484 | SM | 1538.89 | 1.3 | 1 | 1 | 968269.59 | 1 | Active | 1457 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 660 | DDC/Pneumatic System | D306006 | Direct Digital Control Systems | HVAC controls include a hybrid DDC/Pneumatic system with basic pc control, moderate sensor types and quantities as well as pneumatic activation of control valves and dampers. | 1994 | 20 | 2014 | 2026 | 2024-08-11 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 24111 | SM Building | 36.82 | 1.3 | 1 | 1 | 1154097.13 | 1 | Active | 1448 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 659 | DDC/Pneumatic System - Hybrid - Average | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities as well as pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2024-08-01 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SM Building | 36.82 | 1.3 | 1 | 1 | 921755.56 | 1 | Active | 1414 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 723 | Distribution Equipment - Motor Control Centres | D501024 | Main Service Panels | The electrical distribution system is provided with motor control centres for the supply and control of electrical power to the HVAC equipment and other motor loads. | 1982 | 40 | 2022 | 2026 | 2024-08-08 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 17836.48 | 1.3 | 1 | 1 | 92749.7 | 1 | Active | 1439 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 696 | Distribution Switchgears - 15kV, 600A | D501021 | Low Voltage Electrical Service | The electrical distribution system for the building is provided with a 15kV, 600A, switchgear assembly which includes fused interrupter switches, incoming and distribution feeders. | 1997 | 40 | 2037 | 2037 | 2025-06-30 | 1 - Very Good | No significant deficiencies were observed. | 19257 | SM Building | 36.82 | 1.3 | 1 | 1 | 921755.56 | 1 | Active | 1417 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 462 | Domestic Water Distribution - 1972 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4” for main branch piping, water meter, valves, insulation and fittings. | 1972 | 40 | 2012 | 2026 | 2024-07-30 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 13875 | SM Building | 48.15 | 1.3 | 1 | 1 | 868505.63 | 1 | Active | 1411 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 570 | DX Computer Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for the Server Room is provided from a Liebert split DX unit having a cooling capacity of approximately 10 tons. | 2008 | 18 | 2026 | 2026 | 2024-07-24 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 10 | Each | 5488.32 | 1.3 | 1 | 1 | 71348.16 | 1 | Active | 1404 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 458 | Emergency Eyewash Units and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 25 | 2025 | 2026 | 2024-07-16 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 5 | per lavatory | 10976.65 | 1.3 | 1 | 1 | 71348.23 | 1 | Active | 1388 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 888 | Environmental Chambers | E109002 | Basketball Backboards - Fixed | They building is provided with environmental chambers. | 1998 | 30 | 2028 | 2024 | 2026-04-17 | 5 - Very Poor | The staff has reported that the electronics have started to fail and are difficult to source. Replacement is recommended. | 10 | Each | 5418.34 | 1.3 | 1 | 1 | 70438.42 | 2 | Active | 1459 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 292 | Epoxy Wall Paint | C301005 | Painted Wall Covering | The building’s wall finishes include epoxy paint finish located in the Phytotron, CL3, and, animal lab areas. | 2012 | 10 | 2022 | 2025 | 2024-02-17 | 5 - Very Poor | The wall finish is in good condition overall, no major deficiencies were observed. Life cycle replacement can be deferred. | 12317 | SM Building | 50.04 | 1.3 | 1 | 1 | 801245.48 | 1 | Active | 1375 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 877 | Exhaust System - Fume Hoods - 1972 | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1972 | 25 | 1997 | 2026 | 2024-07-25 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 16 | Each | 6859.84 | 1.3 | 1 | 1 | 142684.67 | 1 | Active | 1405 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 878 | Exhaust System - Fume Hoods - 1997 | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1997 | 25 | 2022 | 2026 | 2024-07-26 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 12 | Each | 6859.84 | 1.3 | 1 | 1 | 107013.5 | 1 | Active | 1406 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 801 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with Exit signs to indicate the direction to the means of egress which includes single and double sided LED Exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2012 | 35 | 2047 | 2047 | 2025-11-05 | 1 - Very Good | No significant deficiencies were observed. | 3000 | SM | 275.68 | 1.3 | 1 | 1 | 1075152 | 1 | Active | 1379 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 96 | Exterior Hollow Metal Door - Double Leaf | B203003 | Exterior - Revolving Doors | The exterior doors consist of hollow metal double-doors mounted by butt hinges to metal door frames. | 1972 | 25 | 1997 | 2026 | 2024-07-28 | 4 - Poor | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 1 | Each | 135232.64 | 1.3 | 1 | 1 | 175802.43 | 1 | Active | 1409 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 97 | Exterior Hollow Metal Door - Double Leaf | B203003 | Exterior - Revolving Doors | The exterior doors consist of hollow metal double -doors mounted by butt hinges to metal door frames. | 1994 | 25 | 2019 | 2026 | 2024-08-10 | 4 - Poor | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 1 | Each | 135232.64 | 1.3 | 1 | 1 | 175802.43 | 1 | Active | 1444 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 804 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building includes a fire alarm system that includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The field devices in this block are connected to the control panel in Block H as a separate zone. | 1994 | 20 | 2014 | 2026 | 2024-08-12 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 12056 | SM Building | 60.42 | 1.3 | 1 | 1 | 946950.58 | 1 | Active | 1450 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 814 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-21 | 2 - Good | No significant deficiencies were observed. | 11926 | SM Building | 60.42 | 1.3 | 1 | 1 | 936739.6 | 1 | Active | 1392 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 816 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. | 2016 | 20 | 2036 | 2034 | 2025-04-23 | 2 - Good | No significant deficiencies were observed. | 15403 | SM Building | 60.42 | 1.3 | 1 | 1 | 1209844.04 | 1 | Active | 1399 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 819 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-26 | 2 - Good | No significant deficiencies were observed. | 9279 | SM Building | 60.42 | 1.3 | 1 | 1 | 728828.33 | 1 | Active | 1421 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 830 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2016 | 2016 | 20 | 2036 | 2036 | 2025-06-08 | 1 - Very Good | No significant deficiencies were observed. | 12454 | SM Building | 60.42 | 1.3 | 1 | 1 | 978211.88 | 1 | Active | 1428 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 815 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes a main control panel located in the electrical room, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-22 | 2 - Good | No significant deficiencies were observed. | 11926 | SM Building | 60.42 | 1.3 | 1 | 1 | 936739.6 | 1 | Active | 1393 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 817 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes a main control panel located in the electrical room, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. | 2016 | 20 | 2036 | 2034 | 2025-04-24 | 2 - Good | No significant deficiencies were observed. | 15403 | SM Building | 60.42 | 1.3 | 1 | 1 | 1209844.04 | 1 | Active | 1400 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 820 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system which includes a maim fire alarm control panel, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-27 | 2 - Good | No significant deficiencies were observed. | 9569 | SM Building | 60.42 | 1.3 | 1 | 1 | 751606.67 | 1 | Active | 1422 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 831 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system that includes a main control panel, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 201 | 2016 | 20 | 2036 | 2036 | 2025-06-09 | 1 - Very Good | No significant deficiencies were observed . | 12454 | SM Building | 60.42 | 1.3 | 1 | 1 | 978211.88 | 1 | Active | 1429 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 805 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building includes a fire alarm system that includes all conduit, wire, connections to the main control and annunciator panels, pull stations, audio alarm, visual strobes and smoke detectors. | 1994 | 20 | 2014 | 2026 | 2024-08-13 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 12056 | SM Building | 60.42 | 1.3 | 1 | 1 | 946950.58 | 1 | Active | 1451 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 818 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes all conduit, wire, and connections to the main control and annunciator panels, pull stations, audio alarm, visual strobes and smoke detectors. | 2016 | 20 | 2036 | 2034 | 2025-04-25 | 2 - Good | No significant deficiencies were observed. | 15403 | SM Building | 60.42 | 1.3 | 1 | 1 | 1209844.04 | 1 | Active | 1401 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 821 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes all conduit, wire, and connections to the main control and annunciator panels, pull stations, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-28 | 2 - Good | No significant deficiencies were observed. | 9279 | SM Building | 60.42 | 1.3 | 1 | 1 | 728828.33 | 1 | Active | 1423 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 832 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes all conduit, wire and connections to the control and annunciation panels, pull stations, audio alarms, visual strobes, smoke detectors and control panels. The system has been updated in 2016. | 2016 | 20 | 2036 | 2036 | 2025-06-10 | 1 - Very Good | No significant deficiencies were observed. | 12454 | SM Building | 60.42 | 1.3 | 1 | 1 | 978211.88 | 1 | Active | 1430 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 245 | Fixed Casework - Lab Benches | C103011 | Millwork General | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1998 | 25 | 2023 | 2033 | 2025-04-13 | 2 - Good | The fixed casework is in good condition overall, no significant deficiencies were observed or reported. | 9688 | SM Building | 68.92 | 1.3 | 1 | 1 | 868006.05 | 1 | Active | 1383 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 2 | Foundation Wall and Footings - 10-ft. - Full Basement | A101002 | Low Rise - 1 - 3 Level Building Foundation | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1998 | 75 | 2073 | 2073 | 2023-11-08 | 1 - Very Good | The foundation wall is in good condition overall, no deficiencies were observed. | 29826 | SM Footprint | 304.95 | 1.3 | 1 | 1 | 11824070.31 | 0 | Active | 1380 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 17 | Foundation Wall and Footings - 12-ft. - Full Basement | A202002 | Basement Walls | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1982 | 75 | 2057 | 2057 | 2023-11-16 | 1 - Very Good | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 3096 | SM Footprint | 457.89 | 1.3 | 1 | 1.5 | 2764373.51 | 0 | Active | 1432 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 21 | Foundation Wall and Footings - 12-ft. - Full Basement | A202002 | Basement Walls | The building is a three -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1972 | 75 | 2047 | 2047 | 2025-11-06 | 1 - Very Good | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 5512 | SM Footprint | 457.89 | 1.3 | 1 | 1 | 3281056.58 | 1 | Active | 1384 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 879 | Fume Hood Exhaust Fans | E102007 | Fume Hood Systems | The laboratories are equipped with Fume Hood exhaust fans and ducting. | 1998 | 25 | 2023 | 2026 | 2024-08-16 | 4 - Poor | Not significant deficiencies were observed. Replacement can be deferred. | 10 | Each | 6859.84 | 1.3 | 1 | 1 | 89177.92 | 1 | Active | 1458 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 647 | Hot Water Baseboards | D305004 | Finned Tube Radiation Units | Space heating is provided from perimeter, hot water, baseboard, fin tube, wall convectors and force flow heaters. | 2012 | 30 | 2042 | 2042 | 2025-09-07 | 1 - Very Good | No significant deficiencies were observed. | 800 | SM | 60.96 | 1.3 | 1 | 1 | 63398.4 | 1 | Active | 1378 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 147 | Insulated Metal Panel Roof Cover | B301028 | Metal Roofing | The atrium is protected with a prefinished insulated metal standing seam roof cover. | 1972 | 40 | 2012 | 2026 | 2024-07-14 | 4 - Poor | The roof cover is in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 1722 | SM | 358.76 | 1.3 | 1 | 1 | 803120.14 | 1 | Active | 1386 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 148 | Insulated Metal Panel Roof Cover | B301028 | Metal Roofing | The building's atrium is protected with a corrugated insulated metal standing seam roof cover. | 1972 | 40 | 2012 | 2026 | 2024-07-21 | 4 - Poor | The roof cover is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 1712 | SM | 358.76 | 1.3 | 1 | 1 | 798456.26 | 1 | Active | 1396 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 149 | Insulated Metal Panel Roof Cover | B301028 | Metal Roofing | The atrium is protected with a prefinished insulated metal standing seam roof cover. | 1972 | 40 | 2012 | 2026 | 2024-08-05 | 4 - Poor | The roof cover is in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 2566 | SM | 358.76 | 1.3 | 1 | 1 | 1196751.61 | 1 | Active | 1425 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 221 | Interior Hollow Metal Swing Doors - Single Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors include hollow metal single doors, hinge mounted on metal door frames. | 1998 | 40 | 2038 | 2038 | 2025-08-03 | 1 - Very Good | The building’s interior doors are in good condition overall, no deficiencies were observed. | 28 | Each | 2200 | 1.3 | 1 | 1 | 80080 | 1 | Active | 1382 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 843 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System that includes control panel, arming panels, motion detectors, wiring and conduit. | 2010 | 20 | 2030 | 2030 | 2025-02-13 | 3 - Fair | No significant deficiencies were observed. | 63701 | SM Building | 12.27 | 1.3 | 1 | 1 | 1016094.65 | 1 | Active | 1461 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 69 | Metal Panels | B201028 | Insulated Metal Sandwich Panels | The building includes corrugated non insulated wall panels located on the roof. | 1982 | 40 | 2022 | 2026 | 2024-08-19 | 4 - Poor | The corrugated metal panels require repainting which will be covered under the maintenance budget. LIfecycle replacement can be deferred. | 1830 | SM | 566.46 | 1.3 | 1 | 1 | 1347608.34 | 1 | Active | 1463 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 539 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 1997 | 40 | 2037 | 2037 | 2025-06-28 | 1 - Very Good | No significant deficiencies were observed. | 19257 | SM | 24.55 | 1.3 | 1 | 1 | 614587.16 | 1 | Active | 1413 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 543 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 2000 | 40 | 2040 | 2040 | 2025-08-19 | 1 - Very Good | No significant deficiencies were observed. | 23896 | SM | 24.55 | 1.3 | 1 | 1 | 762640.84 | 1 | Active | 1437 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 177 | One sided windows | C101005 | Interior Windows | The building’s interior windows include one sided monitoring windows located in room 622 and 618. | 2007 | 75 | 2082 | 2057 | 2023-12-26 | 1 - Very Good | The windows are in good condition overall, no deficiencies were observed. | 1055 | SM | 793.05 | 1.3 | 1 | 1 | 1087668.08 | 0 | Active | 1464 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 835 | PA System | D503004 | Public Address and Music Systems | The building is provided with a Public Announcement (PA) System which includes amplifier, microphone, speakers and shield wire in conduit. | 1972 | 15 | 1987 | 2026 | 2024-08-14 | 4 - Poor | No significant deficiencies were observed or reported. Replacement can be deferred. | 35779 | SM Building | 24.55 | 1.3 | 1 | 1 | 1141886.79 | 1 | Active | 1456 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 388 | Painted Ceiling | C303006 | Painted Ceiling Structures | The building’s ceiling finish include painted GWB ceiling. | 2012 | 15 | 2027 | 2027 | 2024-12-28 | 4 - Poor | The ceiling finish is in good condition overall, no major deficiencies were observed. | 26910 | SM | 31.16 | 1.3 | 1 | 1 | 1090070.28 | 1 | Active | 1377 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 296 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2010 | 10 | 2020 | 2026 | 2024-07-29 | 4 - Poor | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 19267 | SM Building | 50.04 | 1.3 | 1 | 1 | 1253356.88 | 1 | Active | 1410 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 649 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2024-07-18 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 200 | Each | 430.08 | 1.3 | 1 | 1 | 111820.8 | 1 | Active | 1390 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 650 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2024-07-22 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 200 | Each | 430.08 | 1.3 | 1 | 1 | 111820.8 | 1 | Active | 1397 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 651 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2024-07-27 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 200 | Each | 430.08 | 1.3 | 1 | 1 | 111820.8 | 1 | Active | 1407 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 834 | Public Address System | D503004 | Public Address and Music Systems | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2000 | 15 | 2015 | 2026 | 2024-07-19 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 24.55 | 1.3 | 1 | 1 | 1141886.79 | 1 | Active | 1391 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 520 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2024-07-31 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SM Building | 34.93 | 1.3 | 1 | 1 | 874441.11 | 1 | Active | 1412 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 526 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1994 | 50 | 2044 | 2044 | 2025-10-03 | 1 - Very Good | No significant deficiencies were observed. | 24111 | SM Building | 34.93 | 1.3 | 1 | 1 | 1094856.4 | 1 | Active | 1447 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 848 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility utilizes a card access security system to monitor strategic doors within the facility and includes controllers, proximity card swipe pads, fob keypads, mag locks and electronic strikes. | 2009 | 15 | 2024 | 2029 | 2025-01-23 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 102897.59 | 1.3 | 1 | 1 | 133766.87 | 1 | Active | 1424 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 849 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a Card Access Security System which monitors strategic doors within the facility and consists of controllers, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2025-02-08 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 102897.59 | 1.3 | 1 | 1 | 133766.87 | 1 | Active | 1394 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 850 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a Card Access System to monitor strategic doors within the facility and includes main control panel, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2025-02-09 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 102897.59 | 1.3 | 1 | 1 | 133766.87 | 1 | Active | 1402 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 851 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a card access security system to monitor strategic doors within the facility and includes controllers, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2025-02-10 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 102897.59 | 1.3 | 1 | 1 | 133766.87 | 1 | Active | 1431 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 852 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a card access security system which monitors strategic doors within the facility and consists of main control panel, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2025-02-11 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 102897.59 | 1.3 | 1 | 1 | 133766.87 | 1 | Active | 1441 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 842 | Security System - CCTV | D503008 | Intrusion Alarm Systems | The building is provided with a CCTV security system which monitors points of egress and includes video recorder, monitoring station, cameras, conduit and cabling. | 2010 | 20 | 2030 | 2030 | 2025-02-12 | 3 - Fair | No significant deficiencies were observed. | 68781 | SM Building | 12.27 | 1.3 | 1 | 1 | 1097125.73 | 1 | Active | 1442 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 252 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 2007 | 20 | 2027 | 2025 | 2024-02-20 | 5 - Very Poor | The buildings’s wayfinding signs are in good condition overall, lifecycle replacement can be deferred. | 89297 | SM Building | 8.5 | 1.3 | 1 | 1 | 986731.85 | 1 | Active | 1452 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 257 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1997 | 20 | 2017 | 2024 | 2026-02-16 | 5 - Very Poor | The wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 63701 | SM Building | 8.5 | 1.3 | 1 | 1 | 703896.05 | 1 | Active | 1403 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 258 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1982 | 20 | 2002 | 2024 | 2026-02-17 | 5 - Very Poor | The building wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 68781 | SM Building | 8.5 | 1.3 | 1 | 1 | 760030.05 | 1 | Active | 1434 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 47 | Soffit - Plaster on Metal Lath | B201008 | Exterior Soffits | C-Blocks bridge soffits are prefinished metal panel soffits. | 1972 | 50 | 2022 | 2026 | 2024-07-20 | 4 - Poor | No significant deficiencies were observed, lifecycle replacement can be deferred. | 6781 | SM | 169.94 | 1.3 | 1 | 1 | 1498072.08 | 1 | Active | 1395 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 5 | Standard Foundations | A101003 | Mid Rise - 4 - 8 Level Building Foundation | The building is a five -story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 2012 | 75 | 2087 | 2087 | 2023-11-10 | 1 - Very Good | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 9243 | SM Footprint | 660.87 | 1.3 | 1 | 1 | 7940947.83 | 0 | Active | 1373 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 7 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1994 | 75 | 2069 | 2069 | 2023-11-12 | 1 - Very Good | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 8073 | SM Footprint | 85.91 | 1.3 | 1 | 1 | 901616.86 | 0 | Active | 1443 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 8 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade, 6-in. thick. | 1998 | 75 | 2073 | 2073 | 2023-11-13 | 1 - Very Good | The slab on grade is in good condition overall, no deficiencies were observed. | 9052 | SM Footprint | 85.91 | 1.3 | 1 | 1 | 1010954.52 | 0 | Active | 1381 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 11 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2025-11-08 | 1 - Very Good | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 7750 | SM Footprint | 85.91 | 1.3 | 1 | 1 | 865543.25 | 1 | Active | 1408 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 317 | Terrazzo Flooring - Cast In Place | C302002 | Terrazzo Floor | The building's floor finishes include terrazzo floor finish located in the 200 floor kitchen. | 1972 | 50 | 2022 | 2026 | 2024-08-06 | 4 - Poor | The floor finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 1184 | SM | 613.67 | 1.3 | 1 | 1 | 944560.86 | 1 | Active | 1426 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 736 | Transformer - 75 KVA | D501026 | Grounding Methods | The building is equipped with two 75 kVA, 600V - 208Y/120V, 3-Phase, transformers on each floor. | 1972 | 50 | 2022 | 2026 | 2024-07-23 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 7 | Each | 13719.68 | 1.3 | 1 | 1 | 124849.09 | 1 | Active | 1398 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 751 | Transformers - 45 KVA | D501026 | Grounding Methods | The building is equipped with two 45 KVA, 600V - 208Y/120V transformers on each floor. | 2008 | 50 | 2058 | 2048 | 2026-01-17 | 1 - Very Good | No significant deficiencies were observed. | 4 | Each | 13719.68 | 1.3 | 1 | 1 | 71342.34 | 1 | Active | 1420 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 737 | Transformers - 75 KVA | D501026 | Grounding Methods | The electrical system is equipped with 75 KVA, 600V - 208Y/120V transformers on each floor. | 1982 | 50 | 2032 | 2026 | 2024-08-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 7 | Each | 13719.68 | 1.3 | 1 | 1 | 124849.09 | 1 | Active | 1440 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 642 | Unit Heaters | D305002 | Unit Heaters (Hydronic) | The HVAC system is provided with unit heaters. | 2012 | 30 | 2042 | 2039 | 2025-08-12 | 1 - Very Good | No significant deficiencies were observed. | 16 | Each | 4300.8 | 1.3 | 1 | 1 | 89456.64 | 1 | Active | 1455 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 340 | Vinyl sheet | C302006 | Masonry and Stone Floor | The building's floor finishes include sheet vinyl flooring located in D205 computer lab | 2009 | 50 | 2059 | 2026 | 2024-08-18 | 4 - Poor | No deficiencies were observed or reported, lifecycle replacement can be deferred. | 1216 | SM | 849.69 | 1.3 | 1 | 1 | 1343189.95 | 1 | Active | 1462 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 360 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include vinyl tile flooring located in the corridors and labs. | 1994 | 15 | 2009 | 2025 | 2024-02-19 | 5 - Very Poor | The vinyl tiles are in good condition overall, lifecycle replacement can be deferred. | 6028 | SM | 119.6 | 1.3 | 1 | 1 | 937233.44 | 1 | Active | 1446 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 899 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include asbestos containing vinyl floor tiles located in the laboratories and the corridors. | 2024 | 15 | 2039 | 2038 |  | 1 - Very Good |  | 5490 | SM | 119.6 | 1.3 | 1 | 1.5 | 1280377.8 | 0 | Active |  | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 486 | Water Heater - Elec - 43 Litre | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a SpaceSaver, 43-Litre, electric, water heater rated at 3.0 KW. | 2010 | 20 | 2030 | 2026 | 2024-07-17 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 8232.48 | 1.3 | 1 | 1 | 10702.22 | 1 | Active | 1389 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 487 | Water Heaters | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by three 454 Liters (120-gal), Rheem, electric, water heaters, each rated at 30000 W. | 2010 | 20 | 2030 | 2026 | 2024-08-07 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 12 | Each | 8232.48 | 1.3 | 1 | 1 | 128426.69 | 1 | Active | 1436 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 674 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems consists of a wet fire standpipe system with backflow protection that Includes distribution piping and shutoff valves. | 1972 | 40 | 2012 | 2026 | 2024-08-02 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SM Building | 32.1 | 1.3 | 1 | 1 | 803594.61 | 1 | Active | 1415 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 675 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection including distribution piping and shutoff valves | 1972 | 40 | 2012 | 2026 | 2024-08-04 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SM Building | 32.1 | 1.3 | 1 | 1 | 1162472.61 | 1 | Active | 1419 | Academic | Brandon Campus West | South
| 01.053 | 5 | Bespin Auditorium | Brandon | 681 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection and Includes distribution piping and shutoff valves | 1994 | 40 | 2034 | 2029 | 2025-01-24 | 3 - Fair | No significant deficiencies were observed. | 24111 | SM Building | 32.1 | 1.3 | 1 | 1 | 1006152.03 | 1 | Active | 1449 | Academic | Brandon Campus West | South
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 398 | Acoustic Ceiling Tiles | C303007 | Suspended Acoustic Panel Ceiling | The building's ceiling finishes include acoustic ceiling tiles located on the 100 floor outside J201 | 2016 | 25 | 2041 | 2036 | 2025-06-06 | 1 - Very Good | The ceiling finish is in good condition overall, no significant deficiencies were observed. | 840 | SM | 113.29 | 1.3 | 1.25 | 1 | 154640.85 | 1 | Active | 1124 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 399 | Acoustic Tile Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | Ceiling finishes located in some offices and laboratories include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 1994 | 25 | 2019 | 2024 | 2026-03-14 | 5 - Very Poor | The ceiling tiles in the second floor are in poor condition, lifecycle replacement is recommended. | 380 | SM | 113.29 | 1.3 | 1.25 | 1 | 69956.58 | 1 | Active | 1099 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 602 | Air Handling Unit - Wine Cellar | D304011 | Refrigerant Distribution Systems | The HVAC system includes an air handling unit with a cooling capacity of 5 tons for the wine cellar with chilled water cooling coils. | 1998 | 45 | 2043 | 2026 | 2024-03-10 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 14500 | SM | 57.59 | 1.3 | 1.25 | 1 | 1356964.38 | 1 | Active | 1017 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 93 | Aluminum Framed IGUs | B202001 | Windows | The building includes punched windows with aluminum frames and insulated glazing units in stone cladding. | 2021 | 35 | 2056 | 2050 | 2026-01-22 | 1 - Very Good |  | 8 | SM | 1387.83 | 1.3 | 1.25 | 1 | 18041.79 | 1 | Active | 1135 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 135 | B301025 - Inverted - Modified Bitumen | B301025 | Inverted - Modified Bitumen | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2021 | 30 | 2051 | 2051 | 2026-01-24 | 1 - Very Good |  | 300 | SM | 321 | 1.3 | 1.25 | 1 | 156487.5 | 1 | Active | 1134 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 144 | B301028 Metal Roofing | B301028 | Metal Roofing | The gable (or hip) roof structure cover is a standing seam (or R-panel) prefinished metal roof. At the roof edge, gutters connected to downspouts that discharge to grade or stormwater sewer system are provided. Add where applicable Ice/snow stops are provided to mitigate the effects of forming ice dams above the main entrance. At the time of the assessment, no roof leaks were reported, and no corrosion or deteriorated metal roof panels were observed. According to information provided, the roof metal panels were replaced in approximately xxxx, and based on age and expected useful life of approximately 30 years, the prefinished metal roof estimated remaining useful life is approximately xx years. OR During the assessment corrosion was observed on the metal roof panels. Based on the observed condition the roof is estimated to have a remaining useful life of approximately xx years | 2021 | 40 | 2061 | 2055 | 2023-12-12 | 1 - Very Good |  | 125 | SM | 358.76 | 1.3 | 1.25 | 1.5 | 109309.69 | 1 | Active | 1133 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 905 | B301028 Metal Roofing | B301028 | Metal Roofing | The gable (or hip) roof structure cover is a standing seam (or R-panel) prefinished metal roof. At the roof edge, gutters connected to downspouts that discharge to grade or stormwater sewer system are provided. Add where applicable Ice/snow stops are provided to mitigate the effects of forming ice dams above the main entrance. At the time of the assessment, no roof leaks were reported, and no corrosion or deteriorated metal roof panels were observed. According to information provided, the roof metal panels were replaced in approximately xxxx, and based on age and expected useful life of approximately 30 years, the prefinished metal roof estimated remaining useful life is approximately xx years. OR During the assessment corrosion was observed on the metal roof panels. Based on the observed condition the roof is estimated to have a remaining useful life of approximately xx years | 2025 | 40 | 2065 | 2064 |  | 1 - Very Good |  | 125 | SM | 358.76 | 1.3 | 1.25 | 1.5 | 109309.69 | 0 | Active |  | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 151 | B301030 - Slate Roofing | B301030 | Slate Roofing | Slate Roof. | 2022 | 50 | 2072 | 2097 | 2023-12-14 | 1 - Very Good |  | 125 | SM | 358.76 | 1.3 | 1.25 | 1.2 | 87447.75 | 0 | Active | 1132 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 546 | Boiler HW - 1982 | D302002 | Hot Water Boilers - Up to 1000 MBH | Heating Hot Water is provided from a Chromalox electric steam boiler rated at 82 MBH (24 KW). | 1982 | 30 | 2012 | 2026 | 2024-04-12 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 82 | MBH | 103.85 | 1.3 | 1.25 | 1 | 13838.01 | 1 | Active | 1092 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 547 | Boiler HW - 1990 | D302002 | Hot Water Boilers - Up to 1000 MBH | Heating medium is provided from a Caloritech electric steam boiler rated at approximately 40 MBH (12 kW). | 1990 | 30 | 2020 | 2026 | 2024-04-13 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 41 | MBH | 103.85 | 1.3 | 1.25 | 1 | 6919.01 | 1 | Active | 1093 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 304 | C301005 - Painted Wall Covering | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2023 | 10 | 2033 | 2033 | 2025-04-07 | 2 - Good |  | 1120 | SM Building | 50.04 | 1.3 | 1.25 | 1 | 91072.8 | 1 | Active | 1137 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 368 | C302004 - Vinyl Tile | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include carpet tile flooring located in offices, conference rooms and miscellaneous spaces. | 2023 | 15 | 2038 | 2038 | 2025-07-31 | 1 - Very Good |  | 500 | SM | 119.6 | 1.3 | 1.25 | 1 | 97175 | 1 | Active | 1140 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 335 | C302005 - Carpet | C302005 | Carpet Floor | The building's floor finish includes asbestos containing vinyl tiles. | 2023 | 10 | 2033 | 2033 | 2025-04-08 | 2 - Good |  | 600 | SM | 103.85 | 1.3 | 1.25 | 1.5 | 151880.63 | 1 | Active | 1138 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 336 | C302005 - Carpet | C302005 | Carpet Floor | The building's floor finishes include vinyl floor tiles located in the labs and the hall ways. | 2023 | 10 | 2033 | 2033 | 2025-04-09 | 2 - Good |  | 860 | SM | 103.85 | 1.3 | 1.25 | 1 | 145130.38 | 1 | Active | 1139 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 603 | Central AHU 1 - Air Handler - TRANE | D304011 | Refrigerant Distribution Systems | The HVAC system has a central air handling unit, AHU-1, with chilled water coils, hot water coils and steam humidification having a approximate capacity of 15000 CFM. | 1998 | 45 | 2043 | 2028 | 2025-01-13 | 3 - Fair | No significant deficiencies were observed. | 14500 | SM | 57.59 | 1.3 | 1.25 | 1 | 1356964.38 | 1 | Active | 1015 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 314 | Ceramic Tile Flooring | C302001 | Ceramic Tile Floor | The building's floor finishes include ceramic tile and base provided in the laundry room. | 2007 | 40 | 2047 | 2037 | 2025-06-13 | 1 - Very Good | The ceramic floor finish is in good condition overall. | 54 | SM | 217.14 | 1.3 | 1.25 | 1 | 19054.04 | 1 | Active | 1109 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 156 | Coffin door roof hatch | B302023 | Hatches | Hollow metal coffin door provides access to building’s roof. | 2007 | 40 | 2047 | 2047 | 2025-10-26 | 1 - Very Good | The roof access door is in good condition overall, no major deficiencies were observed. | 1 | Each | 3047.81 | 1.3 | 1.25 | 1 | 4952.69 | 1 | Active | 1125 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 286 | Concrete stairs | C201001 | Interior Stair Construction | The building includes concrete infilled metal framed stairs with ceramic tile finish that provide access to the 3rd and 4th floors. | 2007 | 75 | 2082 | 2082 | 2026-02-27 | 1 - Very Good | The interior stairs are in good condition overall. | 80 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 137941.7 | 0 | Active | 1130 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 431 | Custodial Sinks | D201004 | Sinks | The plumbing fixtures include floor mounted custodial sinks. | 2012 | 35 | 2047 | 2047 | 2025-10-17 | 1 - Very Good | No significant deficiencies were observed. | 4 | Each | 1433.6 | 1.3 | 1.25 | 1 | 9318.4 | 1 | Active | 1007 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 449 | Custodial Sinks | D201016 | Custodial Sinks | The plumbing fixtures include custodial sinks installed on two floors. | 2000 | 30 | 2030 | 2026 | 2024-03-26 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 2867.2 | 1.3 | 1.25 | 1 | 9318.4 | 1 | Active | 1063 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 453 | Custodial Sinks | D201016 | Custodial Sinks | The plumbing fixtures include flooor-mounted custodial sinks. | 1972 | 30 | 2002 | 2026 | 2024-04-20 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 2867.2 | 1.3 | 1.25 | 1 | 13977.6 | 1 | Active | 1116 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 451 | Custodial Sinks - 1972 | D201016 | Custodial Sinks | The plumbing fixtures include custodial sinks. | 1972 | 30 | 2002 | 2026 | 2024-04-05 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 2867.2 | 1.3 | 1.25 | 1 | 9318.4 | 1 | Active | 1081 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 450 | Custodial Sinks - 2000 | D201016 | Custodial Sinks | The plumbing fixtures include a custodial sink installed on the 2nd floor. | 2000 | 30 | 2030 | 2026 | 2024-04-04 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred | 1 | Each | 2867.2 | 1.3 | 1.25 | 1 | 4659.2 | 1 | Active | 1078 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 445 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include a custodial/utility sink installed in the janitor closet. | 1998 | 30 | 2028 | 2025 | 2024-01-09 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 2867.2 | 1.3 | 1.25 | 1 | 4659.2 | 1 | Active | 1012 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 446 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include a custodial sink installed on the 2nd floor. | 2000 | 30 | 2030 | 2025 | 2024-01-13 | 5 - Very Poor | No significant deficiencies were observed. | 1 | Each | 2867.2 | 1.3 | 1.25 | 1 | 4659.2 | 1 | Active | 1025 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 447 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include a custodial/utility sink installed on the 3rd floor. | 2000 | 30 | 2030 | 2025 | 2024-01-17 | 5 - Very Poor | No significant deficiencies were observed. | 1 | Each | 2867.2 | 1.3 | 1.25 | 1 | 4659.2 | 1 | Active | 1036 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 448 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include a floor mounted custodial sink on the 3rd floor. | 2000 | 30 | 2030 | 2025 | 2024-01-18 | 5 - Very Poor | No significant deficiencies were observed. | 1 | Each | 2867.2 | 1.3 | 1.25 | 1 | 4659.2 | 1 | Active | 1056 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 452 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include custodial/utility sink in the janitor's closet on each floor. | 1990 | 30 | 2020 | 2026 | 2024-04-11 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 2867.2 | 1.3 | 1.25 | 1 | 9318.4 | 1 | Active | 1091 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 890 | Dock Leveller | E109099 | Other Equipment (Other) | The loading dock is provided with a Blue Giant, 6,000LB, dock leveller. | 2012 | 25 | 2037 | 2037 | 2025-06-12 | 1 - Very Good | No significant deficiencies were observed. | 1 | Lump Sum | 5500 | 1.3 | 1.25 | 1 | 8937.5 | 1 | Active | 1006 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 433 | Drinking Water Fountains | D201006 | Drinking Water Fountains (Non-refrigerated) | Plumbing fixtures include wall mounted stainless steel drinking water fountains in the corridors. | 1990 | 30 | 2020 | 2026 | 2024-04-06 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 2150.4 | 1.3 | 1.25 | 1 | 6988.8 | 1 | Active | 1082 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 560 | DX Ductless Split Refrigerant Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for each of the cold rooms is provided by a 2 ton ductless split DX refrigerant unit. | 2008 | 18 | 2026 | 2025 | 2024-01-10 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5488.32 | 1.3 | 1.25 | 1 | 17837.04 | 1 | Active | 1014 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 561 | DX Ductless Split Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for some of the rooms requiring special climate control is provided by a 2 ton Carrier ductless split DX unit. | 2008 | 18 | 2026 | 2025 | 2024-01-23 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5488.32 | 1.3 | 1.25 | 1 | 17837.04 | 1 | Active | 1103 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 564 | DX Ductless Split Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for the Main Electrical Vault is provided by a 2 ton ductless split DX unit. | 2008 | 18 | 2026 | 2026 | 2024-03-28 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5488.32 | 1.3 | 1.25 | 1 | 17837.04 | 1 | Active | 1067 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 565 | DX Ductless Split Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for the walk in cooler is provided by a 2 ton ductless split DX refrigerant unit. | 2008 | 18 | 2026 | 2026 | 2024-04-07 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5488.32 | 1.3 | 1.25 | 1 | 17837.04 | 1 | Active | 1083 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 352 | Epoxy Flooring | C302007 | Painted / Sealed Floor | The building's floor finishes include epoxy floor finish located in room E304. | 2000 | 15 | 2015 | 2024 | 2026-03-06 | 5 - Very Poor | The epoxy floor is in poor condition, lifecycle replacement is recommended. | 754 | SM | 50.98 | 1.3 | 1.25 | 1 | 62463.25 | 1 | Active | 1052 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 303 | Epoxy Wall Paint | C301005 | Painted Wall Covering | The building’s wall finishes include epoxy paint finish located in the Phytotron, CL3, and, animal lab areas. | 2023 | 10 | 2033 | 2033 | 2025-04-06 | 2 - Good |  | 600 | SM Building | 50.04 | 1.3 | 1.25 | 1 | 48789 | 1 | Active | 1136 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 872 | Exhaust System - Fume Hood | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1990 | 25 | 2015 | 2026 | 2024-03-29 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 6859.84 | 1.3 | 1.25 | 1 | 22294.48 | 1 | Active | 1068 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 871 | Exhaust System - Fume Hood - Ductwork/Fan | E102007 | Fume Hood Systems | The exhaust system for the labs includes constant volume fume hoods and exhaust systems. | 1990 | 25 | 2015 | 2026 | 2024-03-12 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 6859.84 | 1.3 | 1.25 | 1 | 22294.48 | 1 | Active | 1026 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 612 | Exhaust System Fans | D304031 | Exhaust Fans | The HVAC system includes exhaust fans installed on the roof and throughout the building. | 1990 | 25 | 2015 | 2026 | 2024-04-14 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 4116.81 | 1.3 | 1.25 | 1 | 13379.63 | 1 | Active | 1094 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 791 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with exit signs showing to indicate the direction to the means of egress and includes single and double sided LED exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2010 | 35 | 2045 | 2026 | 2024-04-18 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 350 | SM | 275.68 | 1.3 | 1.25 | 1 | 156793 | 1 | Active | 1106 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 794 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2000 | 35 | 2035 | 2035 | 2025-05-17 | 2 - Good | No significant deficiencies were observed. | 350 | SM | 275.68 | 1.3 | 1.25 | 1 | 156793 | 1 | Active | 1060 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 799 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2009 | 35 | 2044 | 2044 | 2025-09-30 | 1 - Very Good | No significant deficiencies were observed. | 350 | SM | 275.68 | 1.3 | 1.25 | 1 | 156793 | 1 | Active | 1071 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 103 | Exterior Automatic Openers - Single | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2007 | 15 | 2022 | 2025 | 2024-01-24 | 5 - Very Poor | The exterior door openers are in good condition overall, no deficiencies were observed or reported. Lifecycle replacement can be deferred. | 2 | Each | 8646.76 | 1.3 | 1.25 | 1 | 28101.97 | 1 | Active | 1107 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 105 | Exterior Automatic Openers - Single | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2010 | 15 | 2025 | 2026 | 2024-03-20 | 4 - Poor | The automatic door openers are in good condition and functioning as intended. Lifecycle replacement can be deferred. | 1 | Each | 8646.76 | 1.3 | 1.25 | 1 | 14050.99 | 1 | Active | 1049 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 900 | Exterior Automatic Openers - Single | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2025 | 15 | 2040 | 2039 |  | 1 - Very Good |  | 2 | Each | 8646.76 | 1.3 | 1.25 | 1 | 28101.97 | 0 | Active |  | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 904 | Exterior Automatic Openers - Single | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2025 | 15 | 2040 | 2039 |  | 1 - Very Good |  | 2 | Each | 8646.76 | 1.3 | 1.25 | 1 | 28101.97 | 0 | Active |  | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 112 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior Doors - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 30 | 2002 | 2026 | 2024-03-11 | 4 - Poor | The interior doors are in fair condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 2 | Each | 7088.99 | 1.3 | 1.25 | 1 | 23039.22 | 1 | Active | 1021 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 901 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior Doors - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 2025 | 30 | 2055 | 2054 |  | 1 - Very Good |  | 1 | Each | 7088.99 | 1.3 | 1.25 | 1 | 11519.61 | 0 | Active |  | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 790 | Exterior Lights | D502021 | Interior Lighting Systems (Residential) | The exterior lighting includes wall mounted LED fixtures. | 2012 | 35 | 2047 | 2032 | 2025-03-08 | 2 - Good | No significant deficiencies were observed. | 2500 | SM | 34.93 | 1.3 | 1.25 | 1 | 141903.13 | 1 | Active | 1009 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 45 | Exterior Soffits | B201008 | Exterior Soffits | The building includes prefinished metal soffits located at the loading dock. | 1972 | 50 | 2022 | 2026 | 2024-04-01 | 4 - Poor | The soffits are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 527 | SM | 169.94 | 1.3 | 1.25 | 1 | 145532.37 | 1 | Active | 1073 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 289 | Exterior Stairs - Concrete | C201002 | Exterior (Attached) Stair Construction | The building includes cast in place stairs located at the loading dock area. | 1972 | 40 | 2012 | 2026 | 2024-04-10 | 4 - Poor | The concrete stairs are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 2 | Per Riser | 1332.01 | 1.3 | 1.25 | 1 | 4329.03 | 1 | Active | 1088 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 98 | Exterior Storefront Door - Single Leaf | B203005 | Exterior - Hangar Doors | The exterior doors of hollow metal glazed single - door mounted by butt hinges to metal door frame. | 2005 | 25 | 2030 | 2026 | 2024-03-15 | 4 - Poor | The exterior door is in good condition overall, lifecycle replacement can be deferred. | 1 | Lump Sum | 11288.2 | 1.3 | 1.25 | 1 | 18343.33 | 1 | Active | 1038 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 176 | Faraday cage windows | C101005 | Interior Windows | The building’s interior windows include faraday cage windows located in room 614. | 2007 | 75 | 2082 | 2057 | 2023-12-25 | 1 - Very Good | No significant deficiencies were observed or reported. | 54 | SM | 793.05 | 1.3 | 1.25 | 1 | 69590.14 | 0 | Active | 1127 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 810 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes all conduit, wire, and connections to the main control and annunciator panel, pull stations, audio alarm, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-16 | 2 - Good | No significant deficiencies were observed. | 1108 | SM Building | 60.42 | 1.3 | 1.25 | 1 | 108786.21 | 1 | Active | 1028 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 235 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | The building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 1998 | 25 | 2023 | 2028 | 2025-01-14 | 3 - Fair | The casework is in good condition overall, no significant deficiencies were observed or reported. | 49 | LM | 626.6 | 1.3 | 1.25 | 1 | 49893.03 | 1 | Active | 1019 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 236 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | The building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2000 | 25 | 2025 | 2030 | 2025-01-27 | 3 - Fair | The mill work is in good condition overall, no significant deficiencies were observed. | 39 | LM | 626.6 | 1.3 | 1.25 | 1 | 39710.78 | 1 | Active | 1029 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 237 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2000 | 25 | 2025 | 2030 | 2025-01-29 | 3 - Fair | The millwork is in good condition overall, | 20 | LM | 626.6 | 1.3 | 1.25 | 1 | 20364.5 | 1 | Active | 1037 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 238 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2005 | 25 | 2030 | 2035 | 2025-05-18 | 2 - Good | The millwork is in good condition overall. | 33 | LM | 626.6 | 1.3 | 1.25 | 1 | 33601.43 | 1 | Active | 1061 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 239 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2005 | 25 | 2030 | 2035 | 2025-05-20 | 2 - Good | The mill work is in good condition overall, no significant deficiencies were observed. | 26 | LM | 626.6 | 1.3 | 1.25 | 1 | 26473.85 | 1 | Active | 1086 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 241 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2009 | 25 | 2034 | 2039 | 2025-08-11 | 1 - Very Good | The system is in good condition overall, no significant deficiencies were observed or reported. | 20 | LM | 626.6 | 1.3 | 1.25 | 1 | 20364.5 | 1 | Active | 1072 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 246 | Fixed Casework - Lab Benches | C103011 | Millwork General | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1972 | 25 | 1997 | 2024 | 2026-02-09 | 5 - Very Poor | The casework is in poor condition overall, lifecycle replacement is recommended. | 1023 | SM Building | 68.92 | 1.3 | 1.25 | 1 | 114570.89 | 1 | Active | 1087 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 233 | Gas-Tight Vault Doors | C102099 | Other Interior Doors | The building includes gas tight vault type doors in steel frames located at the CL3 lab at room 568. | 2012 | 40 | 2052 | 2052 | 2026-01-28 | 1 - Very Good | The doors are in good condition overall, no major deficiencies were observed. | 2 | Lump Sum | 5500 | 1.3 | 1.25 | 1 | 17875 | 1 | Active | 1002 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 380 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 15 | 1987 | 2026 | 2024-03-22 | 4 - Poor | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 3122 | SM | 31.16 | 1.3 | 1.25 | 1 | 158082.47 | 1 | Active | 1054 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 381 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include GWB ceiling located in the corridors. | 1972 | 15 | 1987 | 2026 | 2024-04-03 | 4 - Poor | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 2791 | SM | 31.16 | 1.3 | 1.25 | 1 | 141322.29 | 1 | Active | 1077 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 414 | Hand-wash Sinks | D201004 | Sinks | The plumbing fixtures include stainless steel and porcelain hand-wash sinks. | 1972 | 35 | 2007 | 2026 | 2024-04-22 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 1433.6 | 1.3 | 1.25 | 1 | 4659.2 | 1 | Active | 1120 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 413 | Handwash & Kitchen Sinks | D201004 | Sinks | The plumbing fixtures include stainless steel handwash and kitchen sinks. | 1972 | 35 | 2007 | 2026 | 2024-04-19 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 1433.6 | 1.3 | 1.25 | 1 | 4659.2 | 1 | Active | 1115 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 551 | Heat Exchanger - Liquid/Liquid - Plate and Frame | D302011 | Steam Boilers - Over 1000 MBH | The HVAC system includes plate and frame, liquid to liquid, heat exchangers providing heated glycol for the snow melt system near the main entrance. | 2007 | 30 | 2037 | 2037 | 2025-06-14 | 1 - Very Good | No significant deficiencies were observed. | 500 | MBH | 69.99 | 1.3 | 1.25 | 1 | 56866.88 | 1 | Active | 1111 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 552 | Heat Exchangers | D302011 | Steam Boilers - Over 1000 MBH | The HVAC system is provided with plate & frame heat exchangers. | 2012 | 30 | 2042 | 2042 | 2025-08-29 | 1 - Very Good | No significant deficiencies were observed. | 2700 | MBH | 69.99 | 1.3 | 1.25 | 1.49 | 457550.88 | 1 | Active | 1008 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 632 | Humidity Control Equipment - Steam Humidification | D304061 | Fuel-Fired Humidifiers | The HVAC system is equipped with a steam humidification system which supply humidification to the Trane air handler. | 1998 | 20 | 2018 | 2026 | 2024-03-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 6859.84 | 1.3 | 1.25 | 1 | 11147.24 | 1 | Active | 1016 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 633 | Humidity Control Equipment - Steam Humidification | D304061 | Fuel-Fired Humidifiers | The HVAC system is equipped with a NORTEC steam humidification unit for AHU-1. | 1997 | 20 | 2017 | 2026 | 2024-04-08 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 6859.84 | 1.3 | 1.25 | 1 | 11147.24 | 1 | Active | 1084 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 634 | Humidity Control Equipment - Steam Humidification | D304061 | Fuel-Fired Humidifiers | The HVAC system is equipped with a NORTEC steam humidification unit which supplys humidification to the main 2,0000 CFM air handler. | 1998 | 20 | 2018 | 2026 | 2024-04-16 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 6859.84 | 1.3 | 1.25 | 1 | 11147.24 | 1 | Active | 1104 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 198 | Interior Automatic Openers - Single | C102007 | Automatic Door Openers | The building includes automatic openers for single swing doors. | 2010 | 15 | 2025 | 2025 | 2024-01-16 | 5 - Very Poor | The automatic door openers are functioning as intended, no deficiencies were observed. | 2 | Each | 8646.76 | 1.3 | 1.25 | 1 | 28101.97 | 1 | Active | 1031 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 199 | Interior Automatic Openers - Single | C102007 | Automatic Door Openers | The building includes automatic openers for single swing doors. | 1994 | 15 | 2009 | 2025 | 2024-01-19 | 5 - Very Poor | The automatic door openers are functioning as intended, no deficiencies were observed. Lifecycle replacement can be deferred. | 1 | Each | 8646.76 | 1.3 | 1.25 | 1 | 14050.99 | 1 | Active | 1096 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 202 | Interior Automatic Openers - Single | C102007 | Automatic Door Openers | The building includes interior doors with automatic openers for single swing doors located in 300 floor corridor. | 2005 | 15 | 2020 | 2026 | 2024-04-02 | 4 - Poor | The door openers are functioning as intended, life cycle replacement can be deferred. | 2 | Each | 8646.76 | 1.3 | 1.25 | 1 | 28101.97 | 1 | Active | 1074 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 192 | Interior Metal Gate | C101028 | Interior Guardrails and Screens | The building's interior doors include a wrought iron gate located in the 100 floor level wine cellar. | 1998 | 50 | 2048 | 2048 | 2026-01-07 | 1 - Very Good | The iron gate is in good condition overall and functioning as intended. | 10 | LM | 653.07 | 1.3 | 1.25 | 1 | 10612.39 | 1 | Active | 1010 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 274 | Interior Stairs - Cast-In-Place Concrete | C201001 | Interior Stair Construction | The building includes cast-in-place concrete stairs that provide access to different levels of the building. | 1972 | 75 | 2047 | 2047 | 2025-10-19 | 1 - Very Good | The stairs are in fair condition overall, no significant deficiencies were observed or reported. | 120 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 206912.55 | 1 | Active | 1032 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 273 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes cast in place concrete stairs that provides access to different levels in the building. | 1972 | 75 | 2047 | 2047 | 2025-10-18 | 1 - Very Good | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 160 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 275883.4 | 1 | Active | 1022 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 276 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes Cast-in-place concrete stairs that provide access to different levels of the building. | 1972 | 75 | 2047 | 2047 | 2025-10-22 | 1 - Very Good | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 40 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 68970.85 | 1 | Active | 1050 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 278 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes Cast-in-place concrete stairs that provide access to different levels of the building. | 1972 | 75 | 2047 | 2047 | 2025-10-24 | 1 - Very Good | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 40 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 68970.85 | 1 | Active | 1062 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 279 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes cast in place concrete stairs that provides access to different levels in the building. | 1972 | 75 | 2047 | 2047 | 2025-10-25 | 1 - Very Good | The stairs are in good condition overall, no significant deficiencies were observed. | 100 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 172427.13 | 1 | Active | 1075 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 280 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes cast in place concrete stairs that provides access to different levels in the building. | 1982 | 75 | 2057 | 2057 | 2026-02-21 | 1 - Very Good | The cast in place concrete stairs are in good condition overall, no deficiencies were observed. | 80 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 137941.7 | 0 | Active | 1090 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 281 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes Cast-in-place concrete stairs that provide access to different levels of the building. | 1994 | 75 | 2069 | 2069 | 2026-02-22 | 1 - Very Good | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 120 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 206912.55 | 0 | Active | 1097 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 275 | Interior Stairs - Cast-In-Place Concrete Treads - 22 Risers | C201001 | Interior Stair Construction | The building includes cast-in-place concrete stairs that provide access to different levels of the building. | 1972 | 75 | 2047 | 2047 | 2025-10-20 | 1 - Very Good | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 120 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 206912.55 | 1 | Active | 1039 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 282 | Interior Stairs - Concrete Filled Metal Pan Treads | C201001 | Interior Stair Construction | The building includes concrete filled metal pan stairs. | 2005 | 75 | 2080 | 2072 | 2026-02-23 | 1 - Very Good | The stairs are in good condition overall, no significant deficiencies were observed. | 40 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 68970.85 | 0 | Active | 1040 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 283 | Interior Stairs - Concrete Filled Metal Pan Treads | C201001 | Interior Stair Construction | The building's interior stairs are concrete filled metal pan stairs with ceramic tile finish. | 1998 | 75 | 2073 | 2073 | 2026-02-24 | 1 - Very Good | The interior stairs are in good condition overall, no deficiencies were observed. | 60 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 103456.28 | 0 | Active | 1011 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 284 | Interior Stairs - Concrete Filled Metal Pan Treads | C201001 | Interior Stair Construction | Access to the upper levels is via concrete filled metal pan stairs. | 2007 | 75 | 2082 | 2082 | 2026-02-25 | 1 - Very Good | The interior stairs are in good condition overall. | 200 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 344854.25 | 0 | Active | 1108 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 288 | Interior Stairs - Concrete Finish | C201001 | Interior Stair Construction | The building includes two sets of cast-in-place concrete stairs with sealed concrete finish and metal railings. | 2012 | 75 | 2087 | 2087 | 2026-03-01 | 1 - Very Good | The interior stairs are in good condition overall, no major deficiencies were observed. | 120 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 206912.55 | 0 | Active | 1005 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 277 | Interior Stairs - Steel Plate Treads - Air Plenum 100 Floor Level | C201001 | Interior Stair Construction | The building includes a steel plate stairs with 12 risers per flight located in the 100 floor. The stairs are not accessible by the public. | 1972 | 75 | 2047 | 2047 | 2025-10-23 | 1 - Very Good | The stairs are in good condition overall, no significant deficiencies were observed. | 25 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 43106.78 | 1 | Active | 1051 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 287 | Interior Stairs - Tiled | C201001 | Interior Stair Construction | The building includes three sets of cast-in-place concrete stairs with slate tile risers and landings and metal, glass, and plastic railings. | 2012 | 75 | 2087 | 2087 | 2026-02-28 | 1 - Very Good | The slate tiles are starting to deteriorate at the main stairs due to the excessive amount of traffic and it is acting as a tripping hazard. Replacement of the slate tiles are recommended. | 240 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 413825.1 | 0 | Active | 1004 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 685 | IT Room Fire Suppression | D409005 | Chemical Fire Extinguishing Systems (Kitchen Hood) | The IT Server room is provided with a Pyro-Chem FM-200 fire suppression system. | 2015 | 20 | 2035 | 2035 | 2025-05-23 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 5734.41 | 1.3 | 1.25 | 1 | 9318.42 | 1 | Active | 1119 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 422 | Kitchen Sinks | D201004 | Sinks | The plumbing fixtures include kitchen sinks located in the break rooms. | 2007 | 35 | 2042 | 2042 | 2025-08-30 | 1 - Very Good | No significant deficiencies were observed. | 3 | Each | 1433.6 | 1.3 | 1.25 | 1 | 6988.8 | 1 | Active | 1110 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 416 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sinks in the staff rooms on the first and second floors. | 1995 | 35 | 2030 | 2030 | 2025-01-28 | 3 - Fair | No significant deficiencies were observed. | 3 | Each | 1433.6 | 1.3 | 1.25 | 1 | 6988.8 | 1 | Active | 1034 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 417 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sinks in the break rooms. | 2000 | 35 | 2035 | 2035 | 2025-05-16 | 2 - Good | No significant deficiencies were observed. | 3 | Each | 1433.6 | 1.3 | 1.25 | 1 | 6988.8 | 1 | Active | 1057 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 419 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl stainless steel kitchen sinks in the break rooms. | 2000 | 35 | 2035 | 2035 | 2025-05-21 | 2 - Good | No significant deficiencies were observed. | 2 | Each | 1433.6 | 1.3 | 1.25 | 1 | 4659.2 | 1 | Active | 1101 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 421 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single and double bowl kitchen sinks in the staff rooms and medical rooms on the first and second floors. | 2003 | 35 | 2038 | 2038 | 2025-07-27 | 1 - Very Good | No significant deficiencies were observed. | 5 | Each | 1433.6 | 1.3 | 1.25 | 1 | 11648 | 1 | Active | 1024 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 423 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sinks serving the break rooms. | 2009 | 35 | 2044 | 2044 | 2025-09-28 | 1 - Very Good | No significant deficiencies were observed. | 4 | Each | 1433.6 | 1.3 | 1.25 | 1 | 9318.4 | 1 | Active | 1013 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 424 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sinks serving the break rooms. | 2009 | 35 | 2044 | 2044 | 2025-09-29 | 1 - Very Good | No significant deficiencies were observed. | 3 | Each | 1433.6 | 1.3 | 1.25 | 1 | 6988.8 | 1 | Active | 1064 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 426 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sink located in the break rooms. | 2010 | 35 | 2045 | 2045 | 2025-10-07 | 1 - Very Good | No significant deficiencies were observed. | 6 | Each | 1433.6 | 1.3 | 1.25 | 1 | 13977.6 | 1 | Active | 1080 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 418 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. Note that the labs are no longer used as lab sinks. | 2000 | 35 | 2035 | 2035 | 2025-05-19 | 2 - Good | No significant deficiencies were observed. | 4 | Each | 1433.6 | 1.3 | 1.25 | 1 | 9318.4 | 1 | Active | 1079 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 425 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2025-10-06 | 1 - Very Good | No significant deficiencies were observed. | 6 | Each | 1433.6 | 1.3 | 1.25 | 1 | 13977.6 | 1 | Active | 1065 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 780 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system includes wall mounted LED units around the perimeter of the building. | 2014 | 35 | 2049 | 2025 | 2024-01-11 | 5 - Very Poor | No significant deficiencies were observed. | 3000 | SM | 34.93 | 1.3 | 1.25 | 1 | 170283.75 | 1 | Active | 1018 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 781 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system generally includes recessed and surface mounted fixtures, conduit, wire and breakers. | 2000 | 35 | 2035 | 2025 | 2024-01-14 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 2500 | SM | 34.93 | 1.3 | 1.25 | 1 | 141903.13 | 1 | Active | 1027 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 782 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system consists of recessed mounted fixtures around the perimeter of the building. | 2000 | 35 | 2035 | 2026 | 2024-03-25 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1500 | SM | 34.93 | 1.3 | 1.25 | 1 | 85141.88 | 1 | Active | 1059 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 783 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system consists of surface and recessed mounted fixtures, conduit and wire. | 2000 | 35 | 2035 | 2026 | 2024-03-31 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2000 | SM | 34.93 | 1.3 | 1.25 | 1 | 113522.5 | 1 | Active | 1070 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 49 | Metal Panel Soffits and canopy | B201008 | Exterior Soffits | The building includes metal panel soffits and canopy located at the main entrance | 2012 | 50 | 2062 | 2052 | 2026-01-27 | 1 - Very Good | The system is in good condition overall, no deficiencies were observed or reported. | 269 | SM | 169.94 | 1.3 | 1.25 | 1 | 74285.02 | 1 | Active | 1001 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 310 | Metal panels | C301099 | Other Wall Finishes | The building’s interior finishes include insulated metal panel walls located in the 5th floor mechanical room. | 2007 | 30 | 2037 | 2037 | 2025-06-15 | 1 - Very Good | The metal panel wall finish in good condition overall, no major deficiencies were observed. | 2 | Lump Sum | 5500 | 1.3 | 1.25 | 1 | 17875 | 1 | Active | 1128 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 108 | Overhead Doors | B203008 | Exterior - Automatic Door Openers | At the drive-in bay metal insulated segmented overhead doors are provided.The overhead doors are automatically operated. | 2012 | 15 | 2027 | 2037 | 2025-06-11 | 1 - Very Good | No major deficiencies were observed or reported. | 2 | Each | 8646.76 | 1.3 | 1.25 | 1 | 28101.97 | 1 | Active | 1000 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 344 | Painted Floor Finish | C302007 | Painted / Sealed Floor | The building's floor finishes include painted floor finish located at storage rooms and electrical rooms. | 2010 | 15 | 2025 | 2025 | 2024-01-20 | 5 - Very Poor | The painted floor finish is in good condition overall. | 2368 | SM | 50.98 | 1.3 | 1.25 | 1 | 196171.04 | 1 | Active | 1098 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 346 | Painted Floor Finish | C302007 | Painted / Sealed Floor | The building's floor finishes include painted floor finish located at 500 floor storage room and electrical rooms. | 2010 | 15 | 2025 | 2026 | 2024-03-13 | 4 - Poor | The painted floor finish is in good condition overall, lifecycle replacement can be deferred. | 1722 | SM | 50.98 | 1.3 | 1.25 | 1 | 142654.79 | 1 | Active | 1033 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 354 | Painted/ Sealed floors | C302007 | Painted / Sealed Floor | The building includes painted / sealed concrete floors located in the mechanical rooms | 1972 | 15 | 1987 | 2024 | 2026-03-08 | 5 - Very Poor | The painted floor finish has aged and is in poor condition, lifecycle replacement is recommended | 344 | SM | 50.98 | 1.3 | 1.25 | 1 | 28497.82 | 1 | Active | 1113 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 371 | Polished concrete | C302099 | Other Floor Finishes | Majority of the building’s floor is finished with polished concrete. | 2007 | 20 | 2027 | 2027 | 2024-12-12 | 4 - Poor | The polished concrete floor finish is in good condition overall, no major deficiencies were observed. | 1 | Lump Sum | 5500 | 1.3 | 1.25 | 1 | 8937.5 | 1 | Active | 1129 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 285 | Roof access stairs | C201001 | Interior Stair Construction | The building’s interior stairs include metal framed stairs that provide access to the roof. | 2007 | 75 | 2082 | 2082 | 2026-02-26 | 1 - Very Good | The interior stairs are in good condition overall, no major deficiencies were observed. | 25 | Per Riser | 1061.09 | 1.3 | 1.25 | 1 | 43106.78 | 0 | Active | 1126 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 604 | Rooftop Unit - SF-1 | D304011 | Refrigerant Distribution Systems | Cooling and heating for select areas is provided from a YORK, 400,000 BTU, gas fired, rooftop unit with electric cooling. | 2008 | 45 | 2053 | 2038 | 2025-07-28 | 1 - Very Good | No significant deficiencies were observed. | 14500 | SM | 57.59 | 1.3 | 1.25 | 1 | 1356964.38 | 1 | Active | 1043 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 605 | Rooftop Unit - SF-3 | D304011 | Refrigerant Distribution Systems | Cooling and heating for select areas is provided from a YORK, 138,000 BTU, gas fired, rooftop unit with electric cooling. | 2008 | 45 | 2053 | 2038 | 2025-07-29 | 1 - Very Good | No significant deficiencies were observed. | 14500 | SM | 57.59 | 1.3 | 1.25 | 1 | 1356964.38 | 1 | Active | 1044 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 606 | Rooftop Unit - SF-4 | D304011 | Refrigerant Distribution Systems | Cooling and heating for select areas is provided from a YORK, gas fired, rooftop unit. | 2008 | 45 | 2053 | 2038 | 2025-07-30 | 1 - Very Good | No significant deficiencies were observed. | 14500 | SM | 57.59 | 1.3 | 1.25 | 1 | 1356964.38 | 1 | Active | 1045 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 656 | Science stores A/C | D305041 | Heat Pumps | The Science stores is provided with a heat pump. | 2011 | 18 | 2029 | 2029 | 2025-01-21 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 7884.81 | 1.3 | 1.25 | 1 | 12812.82 | 1 | Active | 1118 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 353 | Sealed concrete floor finish | C302007 | Painted / Sealed Floor | The building's floor finish include sealed concrete floor located in the loading dock. | 1972 | 15 | 1987 | 2024 | 2026-03-07 | 5 - Very Poor | The sealed concrete finish is in poor condition, lifecycle replacement is recommended. | 2002 | SM | 50.98 | 1.3 | 1.25 | 1 | 165850.69 | 1 | Active | 1076 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 562 | Split DX Ductless Unit - 1.5 Tons | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for the rock storage room is provided from an LG, 1.5 ton, split DX, condensing unit. | 2008 | 18 | 2026 | 2026 | 2024-03-17 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 5488.32 | 1.3 | 1.25 | 1.5 | 13377.78 | 1 | Active | 1046 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 563 | Split DX Ductless Unit - 2 Tons | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for the rock storage room is provided from a CARRIER, 2 ton, split DX, condensing unit. | 2008 | 18 | 2026 | 2026 | 2024-03-18 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5488.32 | 1.3 | 1.25 | 1 | 17837.04 | 1 | Active | 1047 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 226 | Stainless Steel Doors | C102008 | Interior Doors - Hollow Metal or Wood | Stainless steel doors with stainless steel frames are provided at the MCC bridge. | 2012 | 40 | 2052 | 2052 | 2026-01-29 | 1 - Very Good | The doors are in good condition and are functioning as intended. | 2 | Each | 2200 | 1.3 | 1.25 | 1 | 7150 | 1 | Active | 1003 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 42 | Steel framed guardrails | B201007 | Exterior Guards and Railings | The building includes steel framed guardrails located on the 300 floor | 1982 | 25 | 2007 | 2026 | 2024-04-24 | 4 - Poor | The guardrails are in fair condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 26 | LM | 653.07 | 1.3 | 1.25 | 1 | 27592.21 | 1 | Active | 1122 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 377 | Stucco ceiling | C303006 | Painted Ceiling Structures | The ceiling located on the J430 floor level includes a latex painted ceiling finishes on concrete deck substrate. | 1994 | 15 | 2009 | 2025 | 2024-01-21 | 5 - Very Poor | The ceiling finish is in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 1292 | SM | 31.16 | 1.3 | 1.25 | 1 | 65420.42 | 1 | Active | 1100 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 517 | Sump Pump - Submersible - 1/2 HP | D203006 | Sanitary Waste Ejector Pumps | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 15 | 2012 | 2026 | 2024-03-23 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 7168.01 | 1.3 | 1.25 | 1 | 11648.02 | 1 | Active | 1055 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 519 | Sump Pump - Submersible - 1/2 HP | D203006 | Sanitary Waste Ejector Pumps | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 15 | 2012 | 2047 | 2025-10-21 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 7168.01 | 1.3 | 1.25 | 1 | 11648.02 | 1 | Active | 1041 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 316 | Terrazzo Flooring - Cast In Place | C302002 | Terrazzo Floor | The building's floor finish includes terrazzo floor finish. | 1972 | 50 | 2022 | 2026 | 2024-03-21 | 4 - Poor | The floor finish is in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 183 | SM | 613.67 | 1.3 | 1.25 | 1 | 182490.12 | 1 | Active | 1053 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 638 | Unit Heaters | D305002 | Unit Heaters (Hydronic) | Heating for the loading dock and Main Electrical Vault is provided by suspended, electric, unit heaters. | 1997 | 30 | 2027 | 2026 | 2024-04-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 4300.8 | 1.3 | 1.25 | 1 | 20966.4 | 1 | Active | 1085 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 636 | Unit Heaters - Electric | D305002 | Unit Heaters (Hydronic) | Heating for the rock storage area is provided by a suspended, electric, unit heater. | 1997 | 30 | 2027 | 2026 | 2024-03-19 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 4300.8 | 1.3 | 1.25 | 1 | 6988.8 | 1 | Active | 1048 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 639 | Unit Heaters - Electric | D305002 | Unit Heaters (Hydronic) | Heating for the boiler room and the Main Electrical Vault is each provided by a suspended electric unit heater. | 1990 | 30 | 2020 | 2026 | 2024-04-15 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 4300.8 | 1.3 | 1.25 | 1 | 13977.6 | 1 | Active | 1095 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 637 | Unit Heaters - Electric (Each) | D305002 | Unit Heaters (Hydronic) | Heating for the rock storage area is provided by a suspended, electric, unit heater. | 1985 | 30 | 2015 | 2026 | 2024-03-30 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 4300.8 | 1.3 | 1.25 | 1 | 6988.8 | 1 | Active | 1069 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 640 | Unit Heaters - Hot Water | D305002 | Unit Heaters (Hydronic) | Space heating in mechanical roooms is provided by suspended, forced hot water unit heaters. | 1994 | 30 | 2024 | 2026 | 2024-04-17 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 4300.8 | 1.3 | 1.25 | 1 | 13977.6 | 1 | Active | 1105 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 367 | Vinyl tile | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include vinyl tiles located in room J201 | 2016 | 15 | 2031 | 2031 | 2025-03-07 | 2 - Good | The vinyl tiles are in good condition overall, no significant deficiencies were observed. | 1076 | SM | 119.6 | 1.3 | 1.25 | 1 | 209120.6 | 1 | Active | 1123 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 884 | Walk-in Coolers and Freezers | E109002 | Basketball Backboards - Fixed | The building is provided with walk-in coolers and freezers. | 1997 | 30 | 2027 | 2026 | 2024-04-21 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5418.34 | 1.3 | 1.25 | 1 | 17609.61 | 1 | Active | 1117 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 436 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 2000 | 30 | 2030 | 2025 | 2024-01-22 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 2058.97 | 1.3 | 1.25 | 1 | 10037.48 | 1 | Active | 1102 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 437 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1990 | 30 | 2020 | 2026 | 2024-03-14 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 2058.97 | 1.3 | 1.25 | 1 | 10037.48 | 1 | Active | 1035 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 438 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1995 | 30 | 2025 | 2026 | 2024-03-16 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 2058.97 | 1.3 | 1.25 | 1 | 10037.48 | 1 | Active | 1042 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 439 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1990 | 30 | 2020 | 2026 | 2024-03-24 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 2058.97 | 1.3 | 1.25 | 1 | 10037.48 | 1 | Active | 1058 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 440 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers on each floor. | 1990 | 30 | 2020 | 2026 | 2024-03-27 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 2058.97 | 1.3 | 1.25 | 1 | 13383.31 | 1 | Active | 1066 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 442 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 2000 | 30 | 2030 | 2030 | 2025-01-26 | 3 - Fair | No significant deficiencies were observed. Replacement can be deferred. | 5 | Each | 2058.97 | 1.3 | 1.25 | 1 | 16729.13 | 1 | Active | 1023 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 434 | Water Fountains | D201006 | Drinking Water Fountains (Non-refrigerated) | The plumbing fixtures includes stainless steel water fountains. | 1982 | 30 | 2012 | 2026 | 2024-04-23 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 6 | Each | 2150.4 | 1.3 | 1.25 | 1 | 20966.4 | 1 | Active | 1121 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 499 | Water Treatment System | D202023 | Domestic Water Conditioners - Other | The water for the Boilers are provided from a CULLIGAN water treatment system. | 2012 | 20 | 2032 | 2032 | 2025-03-09 | 2 - Good | No significant deficiencies were observed. | 1 | Lump Sum | 11288.2 | 1.3 | 1.25 | 1 | 18343.33 | 1 | Active | 1112 | Academic | Main Campus | Central
| 04.758 | 1 | Humanities Fine Arts | Vancouver | 321 | Wood laminate flooring | C302003 | Hardwood Floor | The building's floor finishes include wood laminate flooring located in room C301. | 2015 | 30 | 2045 | 2035 | 2025-05-22 | 2 - Good | The floor is in good condition overall. | 323 | SM | 273.79 | 1.3 | 1.25 | 1 | 143705.53 | 1 | Active | 1114 | Academic | Main Campus | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 400 | Acoustic Tile Ceiling - Exposed T-bar - 1972 | C303007 | Suspended Acoustic Panel Ceiling | The building includes suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids located 300 floor. | 1972 | 25 | 1997 | 2024 | 2026-03-15 | 5 - Very Poor | The ceiling tiles are in poor condition overall, lifecycle replacement is recommended. | 1378 | SM | 113.29 | 1.3 | 1.05 | 1 | 213095.09 | 1 | Active | 1167 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 657 | Air Compressors | D306004 | Air Compressors and Dryers (Building Controls) | Lab air compressors consists of two 25HP, ATLAS COPCO, oil-less, rotary tooth, compressors with a 660 gallon receiver and two 106SCFM desiccant air dryers. | 2012 | 15 | 2027 | 2037 | 2025-06-17 | 1 - Very Good | No significant deficiencies were observed. | 2 | Each | 9604 | 1.3 | 1.05 | 1 | 26218.92 | 1 | Active | 1143 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 71 | Aluminum Panel Cladding | B201028 | Insulated Metal Sandwich Panels | The building’s exterior finishes include aluminum panel cladding located at the stairwells above the roof. | 2012 | 40 | 2052 | 2052 | 2026-01-30 | 1 - Very Good | The aluminum cladding exterior wall finish is in good condition overall, no deficiencies were observed. | 301 | SM | 566.46 | 1.3 | 1.05 | 1 | 232738.59 | 1 | Active | 1141 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 134 | B301023 - Conventional - Single Ply Membrane | B301023 | Conventional - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2022 | 20 | 2042 | 2042 | 2025-08-31 | 1 - Very Good |  | 503 | SM | 226.58 | 1.3 | 1.05 | 1.5 | 233353.04 | 1 | Active | 1196 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 143 | B301027 - Asphalt Shingle | B301027 | Asphalt Shingles | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2023 | 15 | 2038 | 2038 | 2025-08-01 | 1 - Very Good |  | 1950 | SM | 75.53 | 1.3 | 1.05 | 1 | 201041.98 | 1 | Active | 1197 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 319 | C302002 - Terrazzo | C302002 | Terrazzo Floor | The building’s floor finishes include carpet tile floor finish located in the offices | 2023 | 50 | 2073 | 2073 | 2026-03-03 | 1 - Very Good |  | 425 | SM | 613.67 | 1.3 | 1.05 | 1 | 356005.31 | 0 | Active | 1199 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 322 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the offices. | 2014 | 10 | 2024 | 2025 | 2024-01-30 | 5 - Very Poor | The carpet tiles are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 1722 | SM | 103.85 | 1.3 | 1.05 | 1 | 244102.54 | 1 | Active | 1185 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 325 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet floor tiles located in the 200 floor. | 2005 | 10 | 2015 | 2026 | 2024-04-30 | 4 - Poor | The carpet tiles are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 1830 | SM | 103.85 | 1.3 | 1.05 | 1 | 259412.11 | 1 | Active | 1157 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 454 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include custodial/utility sinks in the janitor's closet on every other floor. | 2007 | 30 | 2037 | 2032 | 2025-03-10 | 2 - Good | No significant deficiencies were observed. | 5 | Each | 2867.2 | 1.3 | 1.05 | 1 | 19568.64 | 1 | Active | 1189 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 721 | Distribution Equipment - Motor Control Centre | D501024 | Main Service Panels | The electrical distribution system for the building includes a motor control centre for the supply and control of electrical power to HVAC equipment and other motor loads. | 1985 | 40 | 2025 | 2026 | 2024-05-11 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 17836.48 | 1.3 | 1.05 | 1 | 24346.8 | 1 | Active | 1177 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 720 | Distribution Equipment - Motor Control Centres | D501024 | Main Service Panels | The electrical distribution system for the building includes motor control centres for the supply and control of electrical power to HVAC equipment and other motor loads. | 1972 | 40 | 2012 | 2026 | 2024-05-08 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 17836.48 | 1.3 | 1.05 | 1 | 24346.8 | 1 | Active | 1171 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 470 | Domestic Water Distribution - Backflow Preventer - 2012 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes two 4 inch backflow preventer installed in 2012, one on each of the two parallel lines. | 2012 | 40 | 2052 | 2052 | 2026-01-31 | 1 - Very Good | No significant deficiencies were observed. | 2691 | SM Building | 48.15 | 1.3 | 1.05 | 1 | 176865.3 | 1 | Active | 1169 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 391 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 25 | 1997 | 2026 | 2024-05-01 | 4 - Poor | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 1991 | SM | 113.29 | 1.3 | 1.05 | 1 | 307889.93 | 1 | Active | 1158 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 860 | Emergency Battery Pack Lights | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights. | 2000 | 20 | 2020 | 2026 | 2024-05-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SM Building | 6.61 | 1.3 | 1.05 | 1 | 251343.96 | 1 | Active | 1172 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 345 | Epoxy Flooring | C302007 | Painted / Sealed Floor | The building's floor finishes include cement epoxy floor finish located in rooms 216A and 306. | 1998 | 15 | 2013 | 2025 | 2024-01-26 | 5 - Very Poor | The cement epoxy floor is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 4521 | SM | 50.98 | 1.3 | 1.05 | 1 | 314605.99 | 1 | Active | 1144 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 613 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The HVAC system includes centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1997 | 25 | 2022 | 2026 | 2024-05-03 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 4116.81 | 1.3 | 1.05 | 1 | 22477.78 | 1 | Active | 1161 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 795 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with Exit Signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2000 | 35 | 2035 | 2035 | 2025-05-24 | 2 - Good | No significant deficiencies were observed. | 500 | SM | 275.68 | 1.3 | 1.05 | 1 | 188151.6 | 1 | Active | 1148 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 800 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2010 | 35 | 2045 | 2045 | 2025-10-10 | 1 - Very Good | No significant deficiencies were observed. | 600 | SM | 275.68 | 1.3 | 1.05 | 1 | 225781.92 | 1 | Active | 1179 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 896 | Exterior Concrete Accessible Ramp | G203030 | Exterior Ramps - Concrete | The entrance includes a handicap accessible concrete ramp rails on both sides. | 2018 | 40 | 2058 | 2075 | 2026-04-20 | 1 - Very Good | The exterior ramp is in good condition overall, no deficiencies were observed. | 124 | SM | 1161.25 | 1.3 | 1.05 | 1 | 196553.18 | 0 | Active | 1145 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 115 | Exterior Doors - Hollow Metal Doors | B203023 | Exterior Doors - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 2012 | 30 | 2042 | 2037 | 2025-06-16 | 1 - Very Good | No major deficiencies were observed or reported. | 4 | Each | 7088.99 | 1.3 | 1.05 | 1 | 38705.89 | 1 | Active | 1142 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 111 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior Doors - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 30 | 2002 | 2024 | 2023-12-09 | 5 - Very Poor | The doors have aged and are in poor condition, lifecycle replacement is recommended. | 4 | Each | 7088.99 | 1.3 | 1.05 | 1 | 38705.89 | 1 | Active | 1173 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 113 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior Doors - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 30 | 2002 | 2026 | 2024-04-27 | 4 - Poor | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 4 | Each | 7088.99 | 1.3 | 1.05 | 1 | 38705.89 | 1 | Active | 1150 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 104 | Exterior Overhead Sectional Doors | B203008 | Exterior - Automatic Door Openers | The building includes rolling overhead doors located at the loading dock. The doors are automatically operated. | 2000 | 15 | 2015 | 2025 | 2024-01-29 | 5 - Very Poor | The doors are in good condition overall, no significant deficiencies were observed. | 3 | Each | 8646.76 | 1.3 | 1.05 | 1 | 35408.48 | 1 | Active | 1174 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 117 | Exterior Storefront Door - Double Leaf | B203025 | Exterior Doors - Aluminum and Glass | The exterior doors consist of aluminum framed glazed double -doors mounted by butt hinges to aluminum door frames. | 1994 | 35 | 2029 | 2026 | 2024-05-15 | 4 - Poor | The exterior doors are in good condition overall, lifecycle replacement can be deferred. | 1 | Each | 8838.66 | 1.3 | 1.05 | 1 | 12064.77 | 1 | Active | 1184 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 242 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2014 | 25 | 2039 | 2044 | 2025-10-01 | 1 - Very Good | The millwork is in good condition overall, no significant deficiencies were observed. | 53 | LM | 626.6 | 1.3 | 1.05 | 1 | 45331.38 | 1 | Active | 1186 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 243 | Fixed Casework - Lab Benches | C103011 | Millwork General | The building includes metal lab benches with acid resistant countertops. | 1972 | 25 | 1997 | 2026 | 2024-05-04 | 4 - Poor | The lab benches are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred | 1776 | SM Building | 68.92 | 1.3 | 1.05 | 1 | 167078.62 | 1 | Active | 1163 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 1 | Foundation Wall and Footings | A101002 | Low Rise - 1 - 3 Level Building Foundation | The building is a two -storey structure without a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1994 | 75 | 2069 | 2069 | 2023-11-07 | 1 - Very Good | No significant deficiencies were observed or reported. | 7092 | SM Footprint | 304.95 | 1.3 | 1.05 | 1 | 2952092.87 | 0 | Active | 1183 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 18 | Foundation Wall and Footings - 12-ft. - Full Basement | A202002 | Basement Walls | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1972 | 75 | 2047 | 2026 | 2024-05-05 | 4 - Poor | Crack and leaks | 1400 | SM Footprint | 457.89 | 1.3 | 1.05 | 1 | 875027.79 | 1 | Active | 1164 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 187 | Glazed partitions | C101006 | Glazed Partitions | The building includes window units and storefront windows installed in partition openings located on the 300 floor level. | 1982 | 75 | 2057 | 2032 | 2025-03-11 | 2 - Good | The glazed partitions are in fair condition overall, no significant deficiencies were observed | 226 | SM | 1104.6 | 1.3 | 1.05 | 1 | 340758.05 | 1 | Active | 1193 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 200 | Interior Automatic Openers - Single | C102007 | Automatic Door Openers | The building includes automatic openers for single swing doors. | 2010 | 15 | 2025 | 2025 | 2024-01-27 | 5 - Very Poor | The automatic door openers are functioning as intended, no deficiencies were observed. | 3 | Each | 8646.76 | 1.3 | 1.05 | 1 | 35408.48 | 1 | Active | 1151 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 203 | Interior Automatic Openers - Single | C102007 | Automatic Door Openers | The building includes interior doors with automatic openers for single swing doors located in 400 floor office area. | 2005 | 15 | 2020 | 2026 | 2024-04-26 | 4 - Poor | The door openers are functioning as intended, lifecycle replacement can be deferred. | 3 | Each | 8646.76 | 1.3 | 1.05 | 1 | 35408.48 | 1 | Active | 1147 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 197 | Interior Coiling Counter Doors - 6' x 4' | C102006 | Interior - Overhead Doors - Industrial | The building includes coiling counter doors located in room E304. | 2010 | 25 | 2035 | 2040 | 2025-08-16 | 1 - Very Good | The coiling doors are in good condition overall, no significant deficiencies were observed or reported. | 1 | Each | 66600.38 | 1.3 | 1.05 | 1 | 90909.52 | 1 | Active | 1155 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 232 | Interior Doors - Special | C102099 | Other Interior Doors | The interior doors located on the 600 floor level include copper shielded doors. | 2007 | 40 | 2047 | 2047 | 2025-10-28 | 1 - Very Good | The copper shielded doors are functioning as intended. | 3 | Lump Sum | 5500 | 1.3 | 1.05 | 1 | 22522.5 | 1 | Active | 1187 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 195 | Interior Overhead Rolling Doors - 10' x 10' | C102006 | Interior - Overhead Doors - Industrial | The building includes a sectional overhead door that is automatically operated located in the 200 floor kitchen. | 1972 | 25 | 1997 | 2026 | 2024-05-10 | 4 - Poor | The interior door is in good condition overall and functioning as intended. lifecycle replacement can be deferred. | 1 | Each | 66600.38 | 1.3 | 1.05 | 1 | 90909.52 | 1 | Active | 1175 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 180 | Interior Windows | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 300 floor. | 1994 | 75 | 2069 | 2026 | 2024-05-18 | 4 - Poor | No significant deficiencies were observed. Lifecycle replacement can be deferred. | 269 | SM | 793.05 | 1.3 | 1.05 | 1 | 291196.06 | 1 | Active | 1194 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 420 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2000 | 35 | 2035 | 2035 | 2025-05-25 | 2 - Good | No significant deficiencies were observed. | 17 | Each | 1433.6 | 1.3 | 1.05 | 1 | 33266.69 | 1 | Active | 1159 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 427 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2025-10-08 | 1 - Very Good | No significant deficiencies were observed. | 16 | Each | 1433.6 | 1.3 | 1.05 | 1 | 31309.82 | 1 | Active | 1149 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 428 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2025-10-09 | 1 - Very Good | No significant deficiencies were observed. | 16 | Each | 1433.6 | 1.3 | 1.05 | 1 | 31309.82 | 1 | Active | 1153 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 784 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system consists of recessed mounted fixtures with CF lamps, conduit and wire. | 2000 | 35 | 2035 | 2026 | 2024-05-14 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 5000 | SM | 34.93 | 1.3 | 1.05 | 1 | 238397.25 | 1 | Active | 1182 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 788 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system includes surface mounted HID fixtures around the perimeter of the building. | 2007 | 35 | 2042 | 2027 | 2024-12-13 | 4 - Poor | No significant deficiencies were observed. | 3500 | SM | 34.93 | 1.3 | 1.05 | 1 | 166878.08 | 1 | Active | 1190 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 789 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting includes flush mounted fixtures around the perimeter of the building. | 2000 | 35 | 2035 | 2030 | 2025-01-30 | 3 - Fair | No significant deficiencies were observed. | 5000 | SM | 34.93 | 1.3 | 1.05 | 1 | 238397.25 | 1 | Active | 1178 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 142 | Section A | B301026 | Inverted - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2023 | 28 | 2051 | 2051 | 2026-01-25 | 1 - Very Good |  | 850 | SM | 283.23 | 1.3 | 1.05 | 1 | 328617.61 | 1 | Active | 1198 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 253 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1972 | 20 | 1992 | 2024 | 2026-02-12 | 5 - Very Poor | The wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 19267 | SM Building | 8.5 | 1.3 | 1.05 | 1 | 223545.37 | 1 | Active | 1156 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 206 | Single doors | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 1972 | 40 | 2012 | 2026 | 2024-05-06 | 4 - Poor | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 2 | Each | 2200 | 1.3 | 1.05 | 1 | 6006 | 1 | Active | 1165 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 46 | Soffit - Plaster on Metal Lath | B201008 | Exterior Soffits | The buildings overhang soffit is a plaster-on-metal lath soffit. | 1972 | 50 | 2022 | 2026 | 2024-04-25 | 4 - Poor | No significant deficiencies were observed on the exposed soffits. Lifecycle replacment can be deferred. | 1292 | SM | 169.94 | 1.3 | 1.05 | 1 | 299702.79 | 1 | Active | 1146 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 566 | Split Condensing Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for the some of the offices is provided from a split condensing unit having a cooling capacity of 3 tons. | 2008 | 18 | 2026 | 2026 | 2024-04-29 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 5488.32 | 1.3 | 1.05 | 1 | 22474.67 | 1 | Active | 1154 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 510 | Sump Pump - Submersible - 1/2 HP | D203001 | Sanitary Waste and Vent Piping and Fittings | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 50 | 2047 | 2047 | 2025-10-27 | 1 - Very Good | No significant deficiencies were observed. | 2691 | SM Building | 54.76 | 1.3 | 1.05 | 1 | 201145.25 | 1 | Active | 1168 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 518 | Sump Pump - Submersible - 1/2 HP | D203006 | Sanitary Waste Ejector Pumps | The water drainage system includes duplex sanitary sump pump systems. | 2007 | 15 | 2022 | 2026 | 2024-05-16 | 4 - Poor | No significant deficiencies were observed. Lifecycle replacement can be deferred. | 2 | Each | 7168.01 | 1.3 | 1.05 | 1 | 19568.67 | 1 | Active | 1188 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 744 | Transformers - 15 KVA | D501026 | Grounding Methods | The building is equipped with a 15 KVA, 600V - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2026-01-09 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 13719.68 | 1.3 | 1.05 | 1 | 18727.36 | 1 | Active | 1176 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 743 | Transformers - 30 KVA | D501026 | Grounding Methods | The building is equipped with three 30KVA, 600V - 208Y/120V, 3-Phase, transformers. | 2008 | 50 | 2058 | 2048 | 2026-01-08 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 13719.68 | 1.3 | 1.05 | 1 | 18727.36 | 1 | Active | 1162 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 730 | Transformers - 30 KVA & 15 KVA | D501026 | Grounding Methods | The electrical system is equipped with a 30 KVA, 600V - 208Y/120V transformer; and a 15 KVA, 600V - 208Y/120V transformer located in the Main Electrical Room. | 1982 | 50 | 2032 | 2026 | 2024-05-13 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 13719.68 | 1.3 | 1.05 | 1 | 18727.36 | 1 | Active | 1181 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 362 | Vinyl Tile Flooring - 2005 | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include VCT floor finish. | 1997 | 15 | 2012 | 2026 | 2024-04-28 | 4 - Poor | The vinyl tiles are in good condition overall, lifecycle replacement can be deferred. | 1464 | SM | 119.6 | 1.3 | 1.05 | 1 | 239003.86 | 1 | Active | 1152 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 363 | Vinyl Tile Flooring - 2009 | C302022 | Vinyl Tile / Sheet Floor | The building's floor finish includes vinyl tiles located in the 300 floor. | 2009 | 15 | 2024 | 2026 | 2024-05-07 | 4 - Poor | The vinyl tiles are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 1615 | SM | 119.6 | 1.3 | 1.05 | 1 | 263655.21 | 1 | Active | 1166 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 885 | Walk-in Coolers and Freezers | E109002 | Basketball Backboards - Fixed | The building is provided with walk-in coolers and freezers. | 1972 | 30 | 2002 | 2026 | 2024-05-17 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 5418.34 | 1.3 | 1.05 | 1 | 22188.1 | 1 | Active | 1192 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 886 | Walk-in Coolers and Freezers | E109002 | Basketball Backboards - Fixed | The building is provided with walk-in coolers and freezers. | 2007 | 30 | 2037 | 2027 | 2024-12-14 | 4 - Poor | No significant deficiencies were observed. | 3 | Each | 5418.34 | 1.3 | 1.05 | 1 | 22188.1 | 1 | Active | 1191 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 441 | Water Coolers - Wall Mounted (Each) | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 2000 | 30 | 2030 | 2026 | 2024-05-12 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 2058.97 | 1.3 | 1.05 | 1 | 22483.95 | 1 | Active | 1180 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 443 | Water Fountain - Wall Mounted | D201007 | Bidets | The building is provided with ELKAY EZH2O, wall-mounted, drinking fountains. | 2018 | 30 | 2048 | 2033 | 2025-04-10 | 2 - Good | No significant deficiencies were provided. | 8 | Each | 2058.97 | 1.3 | 1.05 | 1 | 22483.95 | 1 | Active | 1195 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 477 | Water Heater - 2013 - 142 L | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 142 litre, electric, SPACESAVER, water heater rated at 3000 W. | 2013 | 20 | 2033 | 2025 | 2024-01-28 | 5 - Very Poor | No significant deficiencies were observed. | 1 | Each | 8232.48 | 1.3 | 1.05 | 1 | 11237.34 | 1 | Active | 1170 | Student Services | Central | Central
| 03.523 | 2 | Kamino Student Ctr | Mount Pearl | 481 | Water Heater - Elec - Residential - 143 Litre | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a 143 litre, SPACESAVER, electric, water heater rated at 3000 W. | 2010 | 20 | 2030 | 2026 | 2024-05-02 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 8232.48 | 1.3 | 1.05 | 1 | 22474.67 | 1 | Active | 1160 | Student Services | Central | Central
| 05.855 | 3 | Lando Gym | Toronto | 389 | Acoustic Tile Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | The building includes suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2005 | 25 | 2030 | 2025 | 2024-02-04 | 5 - Very Poor | The ceiling tiles are in good condition overall, no significant deficiencies were observed. | 2260 | SM | 113.29 | 1.3 | 1.15 | 1 | 382772.92 | 1 | Active | 1242 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 397 | Acoustic Tile Ceiling - Exposed T-bar - 2009 | C303007 | Suspended Acoustic Panel Ceiling | The building includes suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids located 300 floor. | 2009 | 25 | 2034 | 2029 | 2025-01-22 | 3 - Fair | The acoustic ceiling tiles are in good condition overall, no deficiencies were observed or reported. | 2325 | SM | 113.29 | 1.3 | 1.15 | 1 | 393781.88 | 1 | Active | 1237 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 259 | Acoustic Wall Panels | C103033 | Acoustic Panels | Acoustic sound proof wall panels are provided in lecture room 219. | 2012 | 25 | 2037 | 2037 | 2025-06-19 | 1 - Very Good | The panels are in good condition overall, no deficiencies were observed. | 1184 | SM | 217.14 | 1.3 | 1.15 | 1 | 384355.17 | 1 | Active | 1203 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 91 | Aluminum Framed IGUs | B202001 | Windows | The building includes punched windows with aluminum frames and insulated glazing units in stone cladding. | 2012 | 35 | 2047 | 2042 | 2025-09-01 | 1 - Very Good | The windows are in good condition overall, no deficiencies were observed. | 175 | SM | 1387.83 | 1.3 | 1.15 | 1 | 363091.02 | 1 | Active | 1200 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 889 | Autoclaves | E109099 | Other Equipment (Other) | The building is provided with six autoclaves in the CL3 lab with steam sterilizers. | 2012 | 25 | 2037 | 2032 | 2025-03-13 | 2 - Good | No significant deficiencies were observed. | 6 | Lump Sum | 5500 | 1.3 | 1.15 | 1 | 49335 | 1 | Active | 1210 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 106 | Automatic door openers | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2000 | 15 | 2015 | 2026 | 2024-06-10 | 4 - Poor | The door openers are in a fair condition overall, lifecycle replacement can be deferred. | 4 | Each | 8646.76 | 1.3 | 1.15 | 1 | 51707.62 | 1 | Active | 1272 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 145 | B301028 - Metal Roofing | B301028 | Metal Roofing | The building has an inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2022 | 40 | 2062 | 2057 | 2023-12-13 | 1 - Very Good |  | 780 | SM | 358.76 | 1.3 | 1.15 | 1 | 418350.04 | 0 | Active | 1278 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 152 | B301030 - Slate Roofing | B301030 | Slate Roofing | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2023 | 50 | 2073 | 2098 | 2023-12-15 | 1 - Very Good |  | 750 | SM | 358.76 | 1.3 | 1.15 | 1 | 402259.65 | 0 | Active | 1280 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 308 | Bamboo Panel Ceiling | C301022 | Wood Wall Finish | The building’s ceiling finishes include bamboo ceiling finish. | 2012 | 25 | 2037 | 2042 | 2025-09-03 | 1 - Very Good | The ceiling finish is in good condition overall, no major deficiencies were observed. | 915 | SM | 169.94 | 1.3 | 1.15 | 1 | 232465.17 | 1 | Active | 1205 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 311 | Bamboo Panels | C301099 | Other Wall Finishes | The building includes bamboo panels located in lounges and as decorative accents throughout the building. | 2012 | 30 | 2042 | 2042 | 2025-09-02 | 1 - Very Good | No major deficiencies were observed or reported. | 5 | Lump Sum | 5500 | 1.3 | 1.15 | 1 | 41112.5 | 1 | Active | 1204 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 306 | C301021 - Wall Paper | C301021 | Wall Paper | The building's interior finishes include wall paper | 2021 | 20 | 2041 | 2036 | 2025-06-07 | 1 - Very Good |  | 4200 | SM | 50.04 | 1.3 | 1.15 | 1 | 314201.16 | 1 | Active | 1279 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 320 | C302002 - Terrazzo | C302002 | Terrazzo Floor | Terrazzo. | 2023 | 50 | 2073 | 2073 | 2026-03-04 | 1 - Very Good |  | 441 | SM | 613.67 | 1.3 | 1.15 | 1 | 404589.56 | 0 | Active | 1281 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 869 | Capacitor System | D509099 | Other Electrical Systems | The electrical system is provided with two 400kVAR, 600V, Power Survey, power factor correcting capacitor units; and a 313A, 600V, Square D, ReactiVar, harmonic filter unit. | 2012 | 20 | 2032 | 2032 | 2025-03-14 | 2 - Good | No significant deficiencies were observed. | 3 | Lump Sum | 11000 | 1.3 | 1.15 | 1 | 49335 | 1 | Active | 1268 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 326 | Carpet | C302005 | Carpet Floor | The building's floor finishes include broadloom carpet located on the 300 floor. | 2005 | 10 | 2015 | 2026 | 2024-06-04 | 4 - Poor | The carpet is in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 2422 | SM | 103.85 | 1.3 | 1.15 | 1 | 376029.43 | 1 | Active | 1241 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 333 | Carpet Tiles | C302005 | Carpet Floor | The buildings floor finishes include carpet tiles located in some of the offices. | 2018 | 10 | 2028 | 2028 | 2025-01-15 | 3 - Fair | The carpet tiles are in good condition overall, no deficiencies were observed. | 2476 | SM | 103.85 | 1.3 | 1.15 | 1 | 384413.24 | 1 | Active | 1271 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 179 | Ceramic glass | C101005 | Interior Windows | The interior windows include fireproof ceramic glazed windows located on the 5th floor. | 2012 | 75 | 2087 | 2062 | 2023-12-28 | 1 - Very Good | The windows are in good condition overall, no deficiencies were observed. | 441 | SM | 793.05 | 1.3 | 1.15 | 1 | 522853.9 | 0 | Active | 1265 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 549 | Clean Steam Generator | D302003 | Fuel-Fired Forced Air Furnaces | The HVAC system is provided with a 4,000 lb/hr, clean steam generator. It is a steam-to-steam heat exchanger to convert "dirty" steam supplied from one of the steam boilers to "clean steam" with RO water for building humidification. | 2012 | 18 | 2030 | 2042 | 2025-09-04 | 1 - Very Good | No significant deficiencies were observed. | 200 | MBH | 72.24 | 1.3 | 1.15 | 1.7 | 36719.59 | 1 | Active | 1209 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 567 | Condensing Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for the outside walk in cooler is provided by a 4 ton condensing unit. | 2008 | 18 | 2026 | 2026 | 2024-05-19 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 5488.32 | 1.3 | 1.15 | 1 | 32820.15 | 1 | Active | 1212 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 471 | Domestic Water Distribution - Backflow Preventer - 2012 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4 inch backflow preventer installed in 2012. | 2012 | 40 | 2052 | 2052 | 2026-02-01 | 1 - Very Good | No significant deficiencies were observed. | 5382 | SM Building | 48.15 | 1.3 | 1.15 | 1 | 387419.23 | 1 | Active | 1233 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 478 | Electric Water Heater - 2014 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a 284L, 4500W, electric, water heater, JOHN WOOD, model: JW80SDE14S. | 2014 | 20 | 2034 | 2025 | 2024-01-31 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 8232.48 | 1.3 | 1.15 | 1 | 36922.67 | 1 | Active | 1208 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 863 | Emergency Battery Pack Lights | D509003 | Emergency Lighting Systems | The emergency lighting system in some areas includes self-contained battery packs and lights. | 2010 | 20 | 2030 | 2030 | 2025-01-31 | 3 - Fair | No significant deficiencies were observed. | 37954 | SM Building | 6.61 | 1.3 | 1.15 | 1 | 375059.53 | 1 | Active | 1248 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 455 | Emergency Eyewash Units and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 25 | 2025 | 2026 | 2024-05-25 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | per lavatory | 10976.65 | 1.3 | 1.15 | 1 | 49230.28 | 1 | Active | 1220 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 861 | Emergency lighting | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights. | 2007 | 20 | 2027 | 2027 | 2024-12-22 | 4 - Poor | No significant deficiencies were observed. | 46220 | SM Building | 6.61 | 1.3 | 1.15 | 1 | 456743.73 | 1 | Active | 1270 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 387 | Epoxy Painted Ceiling | C303006 | Painted Ceiling Structures | The building’s ceiling finishes include epoxy paint finish located in the Phytotron, CL3, and, animal lab areas. | 2012 | 15 | 2027 | 2027 | 2024-12-15 | 4 - Poor | No deficiencies were observed or reported. | 7320 | SM | 31.16 | 1.3 | 1.15 | 1 | 340996.34 | 1 | Active | 1206 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 609 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The exhaust system consists of centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2000 | 25 | 2025 | 2025 | 2024-02-02 | 5 - Very Poor | No significant deficiencies were observed. | 8 | Each | 4116.81 | 1.3 | 1.15 | 1 | 49237.05 | 1 | Active | 1218 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 610 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The HVAC exhaust ventilation system centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2000 | 25 | 2025 | 2025 | 2024-02-03 | 5 - Very Poor | No significant deficiencies were observed. | 6 | Each | 4116.81 | 1.3 | 1.15 | 1 | 36927.79 | 1 | Active | 1240 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 614 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The HVAC exhaust ventilation system includes centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1998 | 25 | 2023 | 2026 | 2024-05-20 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. There is damage to one fan, the sheet metal shroud should be repaired under normal maintenance. | 6 | Each | 4116.81 | 1.3 | 1.15 | 1 | 36927.79 | 1 | Active | 1213 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 615 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The HVAC exhaust ventilation system centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1990 | 25 | 2015 | 2026 | 2024-06-05 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 6 | Each | 4116.81 | 1.3 | 1.15 | 1 | 36927.79 | 1 | Active | 1247 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 616 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The HVAC system is provided with centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1994 | 25 | 2019 | 2026 | 2024-06-07 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 4116.81 | 1.3 | 1.15 | 1 | 49237.05 | 1 | Active | 1254 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 873 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1976 | 25 | 2001 | 2026 | 2024-06-01 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 5 | Each | 6859.84 | 1.3 | 1.15 | 1 | 51277.3 | 1 | Active | 1234 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 792 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with Exit Signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 1976 | 35 | 2011 | 2026 | 2024-05-27 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 800 | SM | 275.68 | 1.3 | 1.15 | 1 | 329713.28 | 1 | Active | 1225 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 796 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with exit signs on exit doors that includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2000 | 35 | 2035 | 2035 | 2025-05-26 | 2 - Good | No significant deficiencies were observed. | 800 | SM | 275.68 | 1.3 | 1.15 | 1 | 329713.28 | 1 | Active | 1229 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 797 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with exit signs to indicated the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2000 | 35 | 2035 | 2035 | 2025-05-27 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 800 | SM | 275.68 | 1.3 | 1.15 | 1 | 329713.28 | 1 | Active | 1251 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 114 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior Doors - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1976 | 30 | 2006 | 2026 | 2024-05-24 | 4 - Poor | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 5 | Each | 7088.99 | 1.3 | 1.15 | 1 | 52990.2 | 1 | Active | 1219 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 118 | Exterior Storefront Door - Double Leaf | B203025 | Exterior Doors - Aluminum and Glass | The exterior doors consist of hollow metal glazed double -doors mounted by butt hinges to metal frames. | 1976 | 35 | 2011 | 2026 | 2024-05-30 | 4 - Poor | The exterior doors are in fair condition overall and functioning as intended. Lifecycle replacement can be deferred. | 2 | Each | 8838.66 | 1.3 | 1.15 | 1 | 26427.59 | 1 | Active | 1231 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 120 | Exterior Storefront Door - Double Leaf | B203025 | Exterior Doors - Aluminum and Glass | The exterior doors consist of glass metal framed double-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 1982 | 35 | 2017 | 2026 | 2024-06-06 | 4 - Poor | The exterior doors are in fair condition overall, lifecycle replacement can be deferred. | 2 | Each | 8838.66 | 1.3 | 1.15 | 1 | 26427.59 | 1 | Active | 1249 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 119 | Exterior Storefront Door - Single Leaf | B203025 | Exterior Doors - Aluminum and Glass | The exterior doors consist of hollow metal glazed single -doors mounted by butt hinges to metal door frames. | 1976 | 35 | 2011 | 2026 | 2024-06-02 | 4 - Poor | The exterior doors have aged but they are in a fair condition overall, life cycle replacement can be deferred. | 2 | Each | 8838.66 | 1.3 | 1.15 | 1 | 26427.59 | 1 | Active | 1235 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 643 | Fan-coil Units | D305003 | Fan Coil Units | HVAC distribution includes a number of fan-coil units in the corridors near the entrances. | 1998 | 25 | 2023 | 2026 | 2024-05-21 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 7168.01 | 1.3 | 1.15 | 1 | 42864.7 | 1 | Active | 1214 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 240 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2007 | 25 | 2032 | 2037 | 2025-06-20 | 1 - Very Good | The millwork is in good condition overall, no significant deficiencies were observed. | 98 | LM | 626.6 | 1.3 | 1.15 | 1 | 91803.17 | 1 | Active | 1262 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 3 | Foundation Wall and Footings | A101002 | Low Rise - 1 - 3 Level Building Foundation | The building is a three -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1976 | 75 | 2051 | 2047 | 2025-10-30 | 1 - Very Good | No significant deficiencies were observed or reported. | 12114 | SM Footprint | 304.95 | 1.3 | 1.15 | 1 | 5522775.63 | 1 | Active | 1226 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 19 | Foundation Wall and Footings | A202002 | Basement Walls | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1976 | 75 | 2051 | 2047 | 2025-10-31 | 1 - Very Good | No significant deficiencies were observed or reported. | 2232 | SM Footprint | 457.89 | 1.3 | 1.15 | 1 | 1527905.67 | 2 | Active | 1230 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 193 | Glazed Double Doors | C102005 | Interior - Overhead Doors - Standard | The building’s interior doors include glazed double doors with wood frame located in room 209. | 2012 | 25 | 2037 | 2052 | 2026-02-02 | 1 - Very Good | The doors are in good condition overall, no major deficiencies observed. | 3 | Each | 9482.09 | 1.3 | 1.15 | 1 | 42527.17 | 1 | Active | 1267 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 190 | Glazed Guardrails | C101028 | Interior Guardrails and Screens | The building includes glazed guardrails located on the 3rd floor corridor. | 2012 | 50 | 2062 | 2062 | 2023-12-31 | 1 - Very Good | The glazed guardrails are in good condition overall, no major deficiencies were observed. | 82 | LM | 653.07 | 1.3 | 1.15 | 1 | 80059.85 | 0 | Active | 1266 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 382 | Gypsum Board Ceiling | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1976 | 15 | 1991 | 2026 | 2024-06-03 | 4 - Poor | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 9042 | SM | 31.16 | 1.3 | 1.15 | 1 | 421214.34 | 1 | Active | 1238 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 201 | Interior Automatic Openers - Single | C102007 | Automatic Door Openers | The building includes automatic openers for single swing doors located at the universal washrooms. | 2007 | 15 | 2022 | 2025 | 2024-02-07 | 5 - Very Poor | The automatic door openers are in good condition and are functioning as intended. Lifecycle replacement can be deferred. | 4 | Each | 8646.76 | 1.3 | 1.15 | 1 | 51707.62 | 1 | Active | 1257 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 231 | Interior Doors - Special | C102099 | Other Interior Doors | The building includes copper shielded doors locate on the 400 floor. | 1976 | 40 | 2016 | 2026 | 2024-05-22 | 4 - Poor | The copper shielded doors are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 5 | Lump Sum | 5500 | 1.3 | 1.15 | 1 | 41112.5 | 1 | Active | 1215 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 432 | Kitchenette Sinks | D201004 | Sinks | Plumbing fixtures include stainless steel sinks. | 2012 | 35 | 2047 | 2047 | 2025-10-29 | 1 - Very Good | No significant deficiencies were observed. | 24 | Each | 1433.6 | 1.3 | 1.15 | 1 | 51437.57 | 1 | Active | 1207 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 429 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2025-10-11 | 1 - Very Good | No significant deficiencies were observed. | 23 | Each | 1433.6 | 1.3 | 1.15 | 1 | 49294.34 | 1 | Active | 1216 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 785 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system includes wall mounted HID fixtures, around the perimeter of the building which includes conduit and wire. | 1990 | 35 | 2025 | 2026 | 2024-05-29 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 6500 | SM | 34.93 | 1.3 | 1.15 | 1 | 339432.28 | 1 | Active | 1228 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 786 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system recessed mounted fixtures, lamps, conduit and wire. | 2000 | 35 | 2035 | 2026 | 2024-06-08 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 7000 | SM | 34.93 | 1.3 | 1.15 | 1 | 365542.45 | 1 | Active | 1256 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 883 | Loading Dock Equipment | E103003 | Loading Dock Truck Levellers | The building includes a loading dock leveler. | 2007 | 20 | 2027 | 2027 | 2024-12-21 | 4 - Poor | No significent deficiencies were observed. | 1 | Each | 13432.96 | 1.3 | 1.15 | 1 | 20082.28 | 1 | Active | 1263 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 150 | Mechanical Equipment Screens | B301028 | Metal Roofing | The building includes metal framed mechanical equipment screens located on the roof. | 2012 | 40 | 2052 | 2037 | 2025-06-18 | 1 - Very Good | The screens are in good condition overall, no major deficiencies were observed or reported. | 755 | SM | 358.76 | 1.3 | 1.15 | 1 | 404941.38 | 1 | Active | 1201 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 542 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 2000 | 40 | 2040 | 2040 | 2025-08-17 | 1 - Very Good | No significant deficiencies were observed. | 10764 | SM | 24.55 | 1.3 | 1.15 | 1 | 395063.02 | 1 | Active | 1223 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 347 | Painted Concrete | C302007 | Painted / Sealed Floor | The building’s floor finishes include painted/sealed floor finish located in the Mechanical rooms. | 2007 | 15 | 2022 | 2026 | 2024-06-13 | 4 - Poor | The painted floor finish is in excellent condition, no significant deficiencies were observed. | 4790 | SM | 50.98 | 1.3 | 1.15 | 1 | 365070.33 | 1 | Active | 1277 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 188 | Retractable security gates | C101023 | Retractable Partitions - Folding Panel | The building includes retractable security gates located in the 200 floor custodial office | 2000 | 25 | 2025 | 2025 | 2024-02-09 | 5 - Very Poor | The retractable gates are in good condition overall, no significant deficiencies were observed. | 125 | SM | 1954.3 | 1.3 | 1.15 | 1 | 365209.81 | 1 | Active | 1274 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 189 | Retractable security gates | C101023 | Retractable Partitions - Folding Panel | The building’s interior partitions include retractable security gates. | 2012 | 25 | 2037 | 2037 | 2025-06-21 | 1 - Very Good | The retractable security gates are in good condition overall and are functioning as intended. | 125 | SM | 1954.3 | 1.3 | 1.15 | 1 | 365209.81 | 1 | Active | 1264 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 290 | Roof top stairs | C201002 | Exterior (Attached) Stair Construction | The building includes wood framed stairs that provide access to the fume hoods. | 1982 | 40 | 2022 | 2026 | 2024-06-11 | 4 - Poor | The stairs have aged but are functioning as intended. Lifecycle replacement can be deferred. | 20 | Per Riser | 1332.01 | 1.3 | 1.15 | 1 | 39827.1 | 1 | Active | 1275 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 249 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1998 | 20 | 2018 | 2025 | 2024-02-01 | 5 - Very Poor | The wayfinding signage is in good condition overall, lifecycle replacement can be deferred. | 25855 | SM Building | 8.5 | 1.3 | 1.15 | 1 | 328552.41 | 1 | Active | 1211 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 250 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1994 | 20 | 2014 | 2025 | 2024-02-06 | 5 - Very Poor | The wayfinding signs have aged and need to be updated. Lifecycle replacement is recommended. | 24111 | SM Building | 8.5 | 1.3 | 1.15 | 1 | 306390.53 | 1 | Active | 1253 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 254 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1997 | 20 | 2017 | 2024 | 2026-02-13 | 5 - Very Poor | The wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 27857 | SM Building | 8.5 | 1.3 | 1.15 | 1 | 353992.83 | 1 | Active | 1236 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 154 | Skylights | B302021 | Skylights | The building includes skylights with aluminum frame and double-pane insulated glazing. | 1994 | 25 | 2019 | 2025 | 2024-02-05 | 5 - Very Poor | The skylights are in good condition overall, no deficiencies were observed. | 172 | SM | 1661.62 | 1.3 | 1.15 | 1 | 427268.97 | 1 | Active | 1252 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 132 | Small Lower Roofs | B301023 | Conventional - Single Ply Membrane | Built-up roofing with black rubberized flood coat and black aggregate surfacing system on the small lower roofs. | 2012 | 20 | 2032 | 2032 | 2025-03-12 | 2 - Good | The lower roof is good condition, no deficiencies were observed or reported. | 1378 | SM | 226.58 | 1.3 | 1.15 | 1 | 466779.72 | 1 | Active | 1202 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 223 | Solid doors- Double | C102008 | Interior Doors - Hollow Metal or Wood | The building’s interior doors include hollow metal and wood doors with vision panels. | 2007 | 40 | 2047 | 2047 | 2025-11-02 | 1 - Very Good | The interior doors are in good condition overall, no major deficiencies were observed or reported. | 3 | Each | 2200 | 1.3 | 1.15 | 1 | 9867 | 1 | Active | 1258 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 511 | Sump Pump - Submersible - 1/2 HP | D203001 | Sanitary Waste and Vent Piping and Fittings | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 50 | 2047 | 2047 | 2025-11-01 | 1 - Very Good | No significant deficiencies were observed. | 3735 | SM Building | 54.76 | 1.3 | 1.15 | 1 | 305770.26 | 1 | Active | 1243 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 731 | Transformer - 45 KVA | D501026 | Grounding Methods | The building is equipped with a 45 kVA, 600V - 208Y/120V, 3-Phase, transformer on each floor. | 1976 | 50 | 2026 | 2026 | 2024-05-26 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 13719.68 | 1.3 | 1.15 | 1 | 41021.84 | 1 | Active | 1224 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 732 | Transformers - 45 KVA - 1972 | D501026 | Grounding Methods | The building is equipped with a 45 KVA, 600V - 208Y/120V transformer on each floor. | 1976 | 50 | 2026 | 2026 | 2024-05-28 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 13719.68 | 1.3 | 1.15 | 1 | 41021.84 | 1 | Active | 1227 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 745 | Transformers - 45 KVA - 2008 | D501026 | Grounding Methods | The building is equipped with a 45 KVA, 600V - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2026-01-10 | 1 - Very Good | No significant deficiencies were observed. | 2 | Each | 13719.68 | 1.3 | 1.15 | 1 | 41021.84 | 1 | Active | 1273 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 725 | Variable Frequency Drives - Air Handling Units | D501025 | Main Service Disconnects | The supply and return fan motors for the air handling units and the heat recovery units HRU-1 are each equipped with a variable frequency drive. | 2007 | 40 | 2047 | 2027 | 2024-12-20 | 4 - Poor | No significant deficiencies were observed. | 2 | Each | 13719.68 | 1.3 | 1.15 | 1 | 41021.84 | 1 | Active | 1261 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 726 | Variable Frequency Drives - Air Handling Units | D501025 | Main Service Disconnects | The supply and return fan motors for the air handling unit are each equipped with a variable frequency drive. | 2010 | 40 | 2050 | 2030 | 2025-02-01 | 3 - Fair | No significant deficiencies were observed. | 2 | Each | 13719.68 | 1.3 | 1.15 | 1 | 41021.84 | 1 | Active | 1250 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 727 | Variable Frequency Drives - Air Handling Units | D501025 | Main Service Disconnects | The supply and return fan motors for the air handling unit are each equipped with a variable frequency drive. | 2010 | 40 | 2050 | 2030 | 2025-02-02 | 3 - Fair | No significant deficiencies were observed. | 2 | Each | 13719.68 | 1.3 | 1.15 | 1 | 41021.84 | 1 | Active | 1255 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 729 | Variable Frequency Drives - Air Handling Units | D501025 | Main Service Disconnects | The supply and return fan motors for the air handling units serving the G-Block are each equipped with a variable frequency drive. | 2013 | 40 | 2053 | 2033 | 2025-04-11 | 2 - Good | No significant deficiencies were observed. | 2 | Each | 13719.68 | 1.3 | 1.15 | 1 | 41021.84 | 1 | Active | 1246 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 359 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include VCT tiles located in the lunch room (201) and electrical rooms. | 2007 | 15 | 2022 | 2025 | 2024-02-08 | 5 - Very Poor | The vinyl tiles are in a fair condition overall, lifecycle replacement can be deferred. | 2076 | SM | 119.6 | 1.3 | 1.15 | 1 | 371192.95 | 1 | Active | 1259 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 364 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Sheet Floor | The building's floor finish includes asbestos containing vinyl tiles. | 1976 | 15 | 1991 | 2026 | 2024-05-31 | 4 - Poor | The vinyl tiles are in fair condition overall, lifecycle replacement can be deferred. Cost includes a factor for abatement. | 1399 | SM | 119.6 | 1.3 | 1.15 | 1.5 | 375216 | 1 | Active | 1232 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 365 | Vinyl Tiles | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include vinyl tiles located in room J205 and 300 floor corridor. | 2009 | 15 | 2024 | 2026 | 2024-06-12 | 4 - Poor | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 2196 | SM | 119.6 | 1.3 | 1.15 | 1 | 392649.19 | 1 | Active | 1276 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 887 | Walk-in Coolers and Freezers | E109002 | Basketball Backboards - Fixed | The building is provided with walk-in coolers and freezers. | 2012 | 30 | 2042 | 2032 | 2025-03-15 | 2 - Good | No significant deficiencies were observed. | 4 | Each | 5418.34 | 1.3 | 1.15 | 1 | 32401.67 | 1 | Active | 1269 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 494 | Water Heater - 2015 - 322 L | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by an 85-gallon Rheem residential grade electric water heater rated at 15000 W. | 2015 | 20 | 2035 | 2027 | 2024-12-18 | 4 - Poor | No significant deficiencies were observed. | 3 | Each | 8232.48 | 1.3 | 1.15 | 1 | 36922.67 | 1 | Active | 1239 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 498 | Water Heater - 80 Gallon - 1972 | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 323 L (85 gal) RUUD, electric, water heater rated at 45000 W. | 1976 | 20 | 1996 | 2024 | 2026-03-22 | 5 - Very Poor | This equipment has been in service 35 years beyond its rated useful life and the staff has reported that spare parts are difficult to obtain. Replacement is recommended. | 3 | Each | 8232.48 | 1.3 | 1.15 | 1 | 36922.67 | 1 | Active | 1245 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 495 | Water Heater - 85 Gallon - 2011 | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 322 L (85 gal), RHEEM RUUD, electric, water heater rated at 45000 W. | 2011 | 20 | 2031 | 2027 | 2024-12-19 | 4 - Poor | No significant deficiencies were observed. | 3 | Each | 8232.48 | 1.3 | 1.15 | 1 | 36922.67 | 1 | Active | 1244 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 492 | Water Heater - Domestic Hot Water | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water for the building is provided by a RHEEM, 322-Liter (85-gallon), electric, water heater rated at 15000 W located in the custodial room C214. | 2015 | 20 | 2035 | 2027 | 2024-12-16 | 4 - Poor | No significant deficiencies were observed. | 3 | Each | 8232.48 | 1.3 | 1.15 | 1 | 36922.67 | 1 | Active | 1221 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 482 | Water Heater - Elec - 85 Gal | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided from a RHEEM, 322-Liter (85-gallon), electric, water heater rated at 24000 W. | 2006 | 20 | 2026 | 2026 | 2024-05-23 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 8232.48 | 1.3 | 1.15 | 1 | 36922.67 | 1 | Active | 1217 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 493 | Water Heater - Fish Lab | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water for the fish lab is provided by a RHEEM, 322-liter (85-gallon), water heater rated at 15000 W. | 2015 | 20 | 2035 | 2027 | 2024-12-17 | 4 - Poor | No significant deficiencies were observed. | 3 | Each | 8232.48 | 1.3 | 1.15 | 1 | 36922.67 | 1 | Active | 1222 | Athletics | Northeast Campus | East
| 05.855 | 3 | Lando Gym | Toronto | 483 | Water Heater - Gas - 76 Gallon | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 288L (76-gal), John Wood, gas fired, water heater rated at 72MBH. | 2012 | 20 | 2032 | 2026 | 2024-06-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 8232.48 | 1.3 | 1.15 | 1 | 36922.67 | 1 | Active | 1260 | Athletics | Northeast Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 390 | Acoustic Tile Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | Ceiling finishes located in some offices on the 300 floor level include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2007 | 25 | 2032 | 2025 | 2024-02-15 | 5 - Very Poor | The ceiling tiles are in good condition overall, no significant deficiencies were observed. | 4198 | SM | 113.29 | 1.3 | 1 | 1 | 618268.85 | 1 | Active | 1337 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 122 | Aluminum-Framed Storefronts | B203025 | Exterior Doors - Aluminum and Glass | The building includes aluminum framed glazed double-doors with tempered glass door leafs located at the main entrance vestibules. | 2012 | 35 | 2047 | 2037 | 2025-06-22 | 1 - Very Good | The exterior door frames are designed to handle 200 lb doors, however these doors are 300 lbs and are slowly failing. | 4 | Each | 8838.66 | 1.3 | 1 | 1 | 45961.03 | 1 | Active | 1282 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 109 | Automatic Sliding Doors - East and Northwest Entrances | B203021 | Exterior - Overhead Doors - Standard | The building’s exterior doors include automatic sliding doors located at the Northeast side of the building. | 2014 | 25 | 2039 | 2044 | 2025-10-02 | 1 - Very Good | The exterior doors are in good condition overall, no major deficiencies were observed. | 4 | Each | 10385.14 | 1.3 | 1 | 1 | 54002.73 | 1 | Active | 1284 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 225 | B203006 - Glazed Doors - Double | C102008 | Interior Doors - Hollow Metal or Wood | The building includes aluminum framed glazed double-doors with tempered glass door leafs located at the main entrance vestibules. | 2023 | 40 | 2063 | 2048 | 2026-01-16 | 1 - Very Good |  | 4 | Each | 2200 | 1.3 | 1 | 1 | 11440 | 1 | Active | 1369 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 338 | Broadloom Carpet | C302005 | Carpet Floor | The building includes broadloom carpet provided in some offices. | 2007 | 10 | 2017 | 2024 | 2026-03-05 | 5 - Very Poor | The carpets are stained and in poor condition, lifecycle replacement is recommended. | 5274 | SM | 103.85 | 1.3 | 1 | 1 | 712016.37 | 1 | Active | 1355 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 880 | Building and Washroom Exhaust Fans | E102007 | Fume Hood Systems | General building and washroom exhaust consists of roof mounted and in-line exhaust fans with ducting. | 2012 | 25 | 2037 | 2037 | 2025-06-23 | 1 - Very Good | No significant deficiencies were observed. | 6 | Each | 6859.84 | 1.3 | 1 | 1 | 53506.75 | 1 | Active | 1288 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 305 | C301005 - Painted Wall Covering | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, and concrete walls. | 2023 | 10 | 2033 | 2033 | 2025-04-12 | 2 - Good |  | 8000 | SM Building | 50.04 | 1.3 | 1 | 1 | 520416 | 1 | Active | 1370 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 334 | C302005 - Carpet | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the laboratories and the corridors. | 2022 | 10 | 2032 | 2032 | 2025-03-18 | 2 - Good |  | 1900 | SM | 103.85 | 1.3 | 1 | 2 | 513019 | 1 | Active | 1367 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 327 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the offices. | 2015 | 10 | 2025 | 2026 | 2024-06-20 | 4 - Poor | The carpet tiles are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 5242 | SM | 103.85 | 1.3 | 1 | 1 | 707696.21 | 1 | Active | 1307 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 328 | Carpet tiles | C302005 | Carpet Floor | The building includes carpet tile flooring located on the 300 floor | 2014 | 10 | 2024 | 2026 | 2024-07-10 | 4 - Poor | The carpet tiles are in good condition overall, lifecycle replacement can be deferred. | 3552 | SM | 103.85 | 1.3 | 1 | 1 | 479537.76 | 1 | Active | 1362 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 329 | Carpet tiles | C302005 | Carpet Floor | The buildings floor finishes include carpet tiles located in pond inlet hall. | 2016 | 10 | 2026 | 2026 | 2024-07-12 | 4 - Poor | The carpet tiles are in good condition overall, no deficiencies were observed. | 3563 | SM | 103.85 | 1.3 | 1 | 1 | 481022.82 | 1 | Active | 1364 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 557 | Chiller | D303003 | Water Cooled Chillers | Cooling medium is provided by a TRANE, air cooled, chiller installed on the roof with a cooling capacity of 30 tons. | 2010 | 30 | 2040 | 2035 | 2025-05-28 | 2 - Good | No significant deficiencies were observed. | 30 | Ton | 1377.45 | 1.3 | 1 | 1 | 53720.55 | 1 | Active | 1302 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 260 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 2007 | 25 | 2032 | 2026 | 2024-06-14 | 4 - Poor | The washrooms are in fair condition, lifecycle replacement can be deferred. | 1 | Per Lavatory | 21334.7 | 1.3 | 1 | 1 | 27735.11 | 1 | Active | 1292 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 128 | Conventional BUR | B301021 | Conventional - Built-Up Roof | The flat roof structure has a conventional roof assembly system, where the roof membrane is a multi-ply built-up roof membrane protected by a white flood coat and white aggregate surfacing system. Gravel stops completed with pre-finished metal cap flashing are provided at the roof perimeter. | 2023 | 22 | 2045 | 2045 | 2025-10-13 | 1 - Very Good |  | 1500 | SM | 245.47 | 1.3 | 1 | 1 | 478666.5 | 1 | Active | 1372 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 635 | D3042 - Exhaust Ventilation Systems - Room G200 Cryogenic Nitrogen | D305001 | Unit Ventilators | Cryogenic nitrogen is handled in Room G200. Ventilation system was added in 2015 for 28K. | 2015 | 25 | 2040 | 2040 | 2025-08-18 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 16463.84 | 1.3 | 1 | 2.34 | 50083 | 1 | Active | 1333 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 735 | Distribution Transformer - 300kVA | D501026 | Grounding Methods | The electrical system for the building is provided with a 300kVA, 600V - 208Y/120V, 3-Phase transformer. | 2007 | 50 | 2057 | 2026 | 2024-07-11 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 13719.68 | 1.3 | 1 | 1 | 71342.34 | 1 | Active | 1363 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 484 | Domestic Water Tank - 435 Litre | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided from a 435 liter, Rheem Rhuud, domestic cold water storage tank. | 2010 | 20 | 2030 | 2026 | 2024-06-16 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 5 | Each | 8232.48 | 1.3 | 1 | 1 | 53511.12 | 1 | Active | 1297 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 435 | Drinking Water Fountains | D201006 | Drinking Water Fountains (Non-refrigerated) | The building is provided with ELKAY EZH2O drinking water fountains. | 2012 | 30 | 2042 | 2042 | 2025-09-06 | 1 - Very Good | No significant deficiencies were observed. | 24 | Each | 2150.4 | 1.3 | 1 | 1 | 67092.48 | 1 | Active | 1353 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 569 | DX Condensing Units | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling medium is provided by three condensing units, CU-1, CU-2 & CU-3, each having a cooling capacity of 2.5 tons. | 2007 | 18 | 2025 | 2026 | 2024-07-07 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 5488.32 | 1.3 | 1 | 1 | 57078.53 | 1 | Active | 1348 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 864 | Emergency Battery Pack Lights | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights in the corridors and the egress passages. | 2010 | 20 | 2030 | 2030 | 2025-02-05 | 3 - Fair | No significant deficiencies were observed. | 63701 | SM Building | 6.61 | 1.3 | 1 | 1 | 547382.69 | 1 | Active | 1321 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 865 | Emergency Battery Pack Lights | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights in selected areas. | 2010 | 20 | 2030 | 2030 | 2025-02-06 | 3 - Fair | No significant deficiencies were observed. | 68781 | SM Building | 6.61 | 1.3 | 1 | 1 | 591035.13 | 1 | Active | 1341 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 461 | Emergency Eyewash and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed in the sixth floor Mechanical Penthouse and the janitor rooms. | 2007 | 25 | 2032 | 2027 | 2024-12-26 | 4 - Poor | No significant deficiencies were observed. | 4 | per lavatory | 10976.65 | 1.3 | 1 | 1 | 57078.58 | 1 | Active | 1347 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 456 | Emergency Eyewash Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and shower stations installed throughout the building in the labs. | 2007 | 25 | 2032 | 2026 | 2024-06-15 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | per lavatory | 10976.65 | 1.3 | 1 | 1 | 57078.58 | 1 | Active | 1295 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 457 | Emergency Eyewash Units and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2007 | 25 | 2032 | 2026 | 2024-06-26 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | per lavatory | 10976.65 | 1.3 | 1 | 1 | 57078.58 | 1 | Active | 1318 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 348 | Epoxy Flooring | C302007 | Painted / Sealed Floor | The building's floor finishes include epoxy floor finish located in the laboratories. | 2007 | 15 | 2022 | 2026 | 2024-06-21 | 4 - Poor | The floor finish is in good condition overall, lifecycle replacement can be deferred. | 9688 | SM | 50.98 | 1.3 | 1 | 1 | 642062.51 | 1 | Active | 1308 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 881 | Exhaust Fans | E102007 | Fume Hood Systems | The HVAC system is provided with 48,550CFM, Strobic Air, Tri-Stack, 75hp, roof-mounted, exhaust fans. | 2012 | 25 | 2037 | 2037 | 2025-06-24 | 1 - Very Good | No significant deficiencies were observed. | 7 | Each | 6859.84 | 1.3 | 1 | 1 | 62424.54 | 1 | Active | 1289 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 611 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The HVAC exhaust ventilation system consists of centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2007 | 25 | 2032 | 2025 | 2024-02-14 | 5 - Very Poor | No significant deficiencies were observed. | 10 | Each | 4116.81 | 1.3 | 1 | 1 | 53518.53 | 1 | Active | 1311 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 617 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The HVAC system is provided with centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2007 | 25 | 2032 | 2026 | 2024-06-27 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 12 | Each | 4116.81 | 1.3 | 1 | 1 | 64222.24 | 1 | Active | 1319 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 619 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans | The HVAC equipment is provided with an exhaust ventilation system with centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2007 | 25 | 2032 | 2032 | 2025-03-16 | 2 - Good | No significant deficiencies were observed. | 12 | Each | 4116.81 | 1.3 | 1 | 1 | 64222.24 | 1 | Active | 1349 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 874 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. Note: System cost represents a 6 foot long fume hood. | 2007 | 25 | 2032 | 2026 | 2024-06-17 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 6859.84 | 1.3 | 1 | 1 | 71342.34 | 1 | Active | 1298 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 875 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood exhaust systems with ducting. | 2007 | 25 | 2032 | 2026 | 2024-06-24 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 7 | Each | 6859.84 | 1.3 | 1 | 1 | 62424.54 | 1 | Active | 1312 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 107 | Exterior Doors - Automatic Door Operators | B203008 | Exterior - Automatic Door Openers | Automatic door operators are provided a the main entrance vestibules. | 2012 | 15 | 2027 | 2027 | 2024-12-23 | 4 - Poor | The automatic door openers are functioning as intended, no major deficiencies were observed. | 9 | Each | 8646.76 | 1.3 | 1 | 1 | 101167.09 | 1 | Active | 1283 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 116 | Exterior Storefront Door - Double Leaf | B203025 | Exterior Doors - Aluminum and Glass | The building's exterior doors includes aluminum framed glazed double doors. | 2007 | 35 | 2042 | 2025 | 2024-02-11 | 5 - Very Poor | The exterior doors are in good condition overall and functioning as intended, lifecycle replacement can be deferred. | 3 | Each | 8838.66 | 1.3 | 1 | 1 | 34470.77 | 1 | Active | 1291 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 123 | Exterior Storefront Door - Double Leaf | B203025 | Exterior Doors - Aluminum and Glass | The exterior doors consist of hollow metal glazed double -doors mounted by butt hinges to metal door frames. | 2007 | 35 | 2042 | 2038 | 2025-08-02 | 1 - Very Good | The exterior doors have aged and are in poor condition, lifecycle replacement is recommended. | 3 | Each | 8838.66 | 1.3 | 1 | 1 | 34470.77 | 1 | Active | 1317 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 99 | Exterior Storefront Door - Single Leaf | B203005 | Exterior - Hangar Doors | The exterior doors consist of glass metal framed single-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 2007 | 25 | 2032 | 2026 | 2024-07-04 | 4 - Poor | The exterior doors are in fair condition overall, lifecycle replacement can be deferred. | 4 | Lump Sum | 11288.2 | 1.3 | 1 | 1 | 58698.64 | 1 | Active | 1336 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 227 | Fibreglass Reinforced Polyester Door | C102008 | Interior Doors - Hollow Metal or Wood | Fiberglass reinforced polyester door with stainless steel frames, some with glass lites are provided at rooms 569 & 576. | 2012 | 40 | 2052 | 2052 | 2026-02-03 | 1 - Very Good | No deficiencies were observed or reported. | 12 | Each | 2200 | 1.3 | 1 | 1 | 34320 | 1 | Active | 1285 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 811 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building iis provided with a fire alarm system which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-17 | 2 - Good | No significant deficiencies were observed. | 6415 | SM Building | 60.42 | 1.3 | 1 | 1 | 503872.59 | 1 | Active | 1326 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 812 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system which includes a maim fire alarm control panel, an annunciator panel at the main entrance, and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-18 | 2 - Good | No significant deficiencies were observed. | 6415 | SM Building | 60.42 | 1.3 | 1 | 1 | 503872.59 | 1 | Active | 1327 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 813 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes all conduit, wire, and connections to the main control panel, annunciation panel, pull stations, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-19 | 2 - Good | No significant deficiencies were observed. No photo is available. | 6415 | SM Building | 60.42 | 1.3 | 1 | 1 | 503872.59 | 1 | Active | 1328 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 244 | Fixed Casework - Lab Benches | C103011 | Millwork General | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 2007 | 25 | 2032 | 2026 | 2024-06-29 | 4 - Poor | The fixed caework is in fair condition overall, lifecycle replacement can be deferred. | 5167 | SM Building | 68.92 | 1.3 | 1 | 1 | 462942.53 | 1 | Active | 1322 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 247 | Fixed Casework - Lab Benches | C103011 | Millwork General | The building includes metal lab benches with acid resistant countertops. | 2007 | 25 | 2032 | 2024 | 2026-02-10 | 5 - Very Poor | The millwork has aged and is in poor condition, lifecycle replacement is recommended. | 6781 | SM Building | 68.92 | 1.3 | 1 | 1 | 607550.48 | 1 | Active | 1315 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 891 | Fixed Casework - Lab Benches | E201003 | Bleachers | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 2007 | 25 | 2032 | 2026 | 2024-06-19 | 4 - Poor | The millwork is in fair condition overall, lifecycle replacement can be deferred. | 70 | Per Seat | 180.61 | 1.3 | 1 | 1 | 16435.51 | 1 | Active | 1305 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 687 | FM200 System - High Density | D409099 | Other Fire Protection Systems | The fire protection systems include a clean air PyroChem system for the server room. | 2010 | 20 | 2030 | 2026 | 2024-07-02 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Lump Sum | 11000 | 1.3 | 1 | 1 | 57200 | 1 | Active | 1325 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 20 | Foundation Wall and Footings | A202002 | Basement Walls | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 2007 | 75 | 2082 | 2047 | 2025-11-03 | 1 - Very Good | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 2520 | SM Footprint | 457.89 | 1.3 | 1 | 1 | 1500047.64 | 1 | Active | 1331 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 4 | Foundation Wall and Footings - 14-ft. - Full Basement | A101003 | Mid Rise - 4 - 8 Level Building Foundation | The building is a five -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 2007 | 75 | 2082 | 2082 | 2023-11-09 | 1 - Very Good | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 6057 | SM Footprint | 660.87 | 1.3 | 1 | 1 | 5203756.47 | 0 | Active | 1345 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 876 | Fume Hoods | E102007 | Fume Hood Systems | The labs are provided with exhaust fume hoods with ducting. | 2007 | 25 | 2032 | 2026 | 2024-07-13 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 7 | Each | 6859.84 | 1.3 | 1 | 1 | 62424.54 | 1 | Active | 1365 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 312 | Glazed wall panels | C301099 | Other Wall Finishes | The building’s wall finishes include glazed wall panels located near the main entrance. | 2012 | 30 | 2042 | 2042 | 2025-09-05 | 1 - Very Good | No major deficiencies were observed or reported. | 10 | Lump Sum | 5500 | 1.3 | 1 | 1 | 71500 | 1 | Active | 1352 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 378 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling located in the corridors. | 2007 | 15 | 2022 | 2025 | 2024-02-12 | 5 - Very Poor | The GWB ceiling finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 11873 | SM | 31.16 | 1.3 | 1 | 1 | 480951.48 | 1 | Active | 1293 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 383 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 2007 | 15 | 2022 | 2026 | 2024-06-22 | 4 - Poor | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 12153 | SM | 31.16 | 1.3 | 1 | 1 | 492293.72 | 1 | Active | 1309 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 384 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include GWB ceiling located in the corridors. | 2007 | 15 | 2022 | 2026 | 2024-07-05 | 4 - Poor | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 11410 | SM | 31.16 | 1.3 | 1 | 1 | 462196.28 | 1 | Active | 1338 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 410 | Handicap Lift - 3-Storey | D101004 | Wheelchair Lifts | The conveying equipment includes a 3-storey, hydraulic, 454Kg (1000LBS), handicap lift and is rated at 2.6 HP. | 2007 | 25 | 2032 | 2028 | 2025-01-16 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 43005.78 | 1.3 | 1 | 1 | 55907.51 | 1 | Active | 1294 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 196 | Interior Coiling Counter Doors - 6' x 4' | C102006 | Interior - Overhead Doors - Industrial | The building’s interior doors include coiling counter doors located in room 600B. | 2007 | 25 | 2032 | 2037 | 2025-06-26 | 1 - Very Good | The coiling doors are in good condition overall, no major deficiencies were observed. | 2 | Each | 66600.38 | 1.3 | 1 | 1 | 173160.99 | 1 | Active | 1346 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 207 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 2007 | 40 | 2047 | 2026 | 2024-06-30 | 4 - Poor | The double doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 4 | Each | 2200 | 1.3 | 1 | 1 | 11440 | 1 | Active | 1323 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 219 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 2007 | 40 | 2047 | 2034 | 2025-04-20 | 2 - Good | The doors are in good condition overall, no significant deficiencies were observed. | 6 | Each | 2200 | 1.3 | 1 | 1 | 17160 | 1 | Active | 1342 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 194 | Interior Rolling Doors - | C102006 | Interior - Overhead Doors - Industrial | The building includes interior rolling doors located in the corridor. | 2007 | 25 | 2032 | 2025 | 2024-02-16 | 5 - Very Poor | The doors are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 2 | Each | 66600.38 | 1.3 | 1 | 1 | 173160.99 | 1 | Active | 1343 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 181 | Interior Windows - Metal | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 300 floor. | 2007 | 75 | 2082 | 2026 | 2024-07-03 | 4 - Poor | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 646 | SM | 793.05 | 1.3 | 1 | 1 | 666003.39 | 1 | Active | 1329 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 846 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System and includes main control panel, ultrasonic detectors, arming panels, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2015 | 20 | 2035 | 2035 | 2025-05-29 | 2 - Good | No significant deficiencies were observed. | 35779 | SM Building | 12.27 | 1.3 | 1 | 1 | 570710.83 | 1 | Active | 1354 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 847 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System which includes main control panel, motion detectors, arming panels, wiring and conduit. | 2015 | 20 | 2035 | 2035 | 2025-05-30 | 2 - Good | No significant deficiencies were observed. | 46220 | SM Building | 12.27 | 1.3 | 1 | 1 | 737255.22 | 1 | Active | 1357 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 430 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2025-10-12 | 1 - Very Good | No significant deficiencies were observed. | 30 | Each | 1433.6 | 1.3 | 1 | 1 | 55910.4 | 1 | Active | 1296 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 787 | Lighting Fixtures - Exterior | D502021 | Interior Lighting Systems (Residential) | The exterior lighting system consists of surface and recessed mounted fixtures, conduit and wire. | 2007 | 35 | 2042 | 2026 | 2024-06-25 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 10000 | SM | 34.93 | 1.3 | 1 | 1 | 454090 | 1 | Active | 1313 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 779 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts including conduit and wire. | 2024 | 35 | 2059 | 2051 | 2026-01-26 | 1 - Very Good |  | 3526 | SM Building | 101.96 | 1.3 | 1 | 1 | 467364.25 | 1 | Active | 1368 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 39 | Mechanical equipment screens | B201005 | Exterior Louvers and Screens | The building includes corrugated metal mechanical equipment screen with metal frame. | 2007 | 50 | 2057 | 2026 | 2024-07-08 | 4 - Poor | Uniform corrosion was observed on the mechanical equipment screen. Maintenance is recommended to extend the life of the screen which will be covered under the maintenance budget. | 463 | SM | 802.49 | 1.3 | 1 | 1 | 483018.73 | 1 | Active | 1358 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 68 | Metal Panel | B201028 | Insulated Metal Sandwich Panels | The building exterior wall includes insulated corrugated metal panel system located on the 200 floor. | 2007 | 40 | 2047 | 2056 | 2023-11-28 | 1 - Very Good | The exterior wall system is in good condition overall, no deficiencies were observed or reported. | 1109 | SM | 566.46 | 1.3 | 1 | 1 | 816665.38 | 0 | Active | 1360 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 722 | Motor Control Centres | D501024 | Main Service Panels | The electrical distribution system is provided with motor control centres for the supply and control of electrical power to HVAC equipment and other motor loads. | 2007 | 40 | 2047 | 2026 | 2024-07-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 17836.48 | 1.3 | 1 | 1 | 46374.85 | 1 | Active | 1359 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 648 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating in the washrooms and corridors. | 2007 | 18 | 2025 | 2026 | 2024-07-06 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 100 | Each | 430.08 | 1.3 | 1 | 1 | 55910.4 | 1 | Active | 1344 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 43 | Railings | B201007 | Exterior Guards and Railings | The building include aluminum walkway/ guardrails located on the rooftop. | 2007 | 25 | 2032 | 2030 | 2025-02-07 | 3 - Fair | The System is in good condition overall, no deficiencies were observed. | 89 | LM | 653.07 | 1.3 | 1 | 1 | 75560.2 | 1 | Active | 1356 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 44 | Roof Mounted Steps and Walkway | B201007 | Exterior Guards and Railings | The roof includes a set of stairs with 6 steel plate treads, steel grate walkway and pipe railing. | 2010 | 25 | 2035 | 2050 | 2026-01-23 | 1 - Very Good | The steel grate walkway is in good condition overall, no significant deficiencies were observed. | 92 | LM | 653.07 | 1.3 | 1 | 1 | 78107.17 | 1 | Active | 1300 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 153 | Section B - Green Roofing | B301032 | Green Roofing | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2024 | 30 | 2054 | 2054 | 2023-12-16 | 1 - Very Good |  | 850 | SM | 632.55 | 1.3 | 1 | 1 | 698967.75 | 1 | Active | 1371 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 840 | Security System - CCTV | D503008 | Intrusion Alarm Systems | The building is provided with a CCTV Security System which monitors points of egress and includes video recorder, monitoring station, cameras, conduit and cabling. | 2010 | 20 | 2030 | 2030 | 2025-02-03 | 3 - Fair | No significant deficiencies were observed. | 35779 | SM Building | 12.27 | 1.3 | 1 | 1 | 570710.83 | 1 | Active | 1304 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 841 | Security System - CCTV | D503008 | Intrusion Alarm Systems | The building is provided with a CCTV Security System that monitors points of egress and includes video recorder, monitoring station, cameras, conduit and cabling. | 2010 | 20 | 2030 | 2030 | 2025-02-04 | 3 - Fair | No significant deficiencies were observed. | 46220 | SM Building | 12.27 | 1.3 | 1 | 1 | 737255.22 | 1 | Active | 1314 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 251 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 2007 | 20 | 2027 | 2025 | 2024-02-13 | 5 - Very Poor | The building wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 37017 | SM Building | 8.5 | 1.3 | 1 | 1 | 409037.85 | 1 | Active | 1301 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 255 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 2007 | 20 | 2027 | 2024 | 2026-02-14 | 5 - Very Poor | The wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 46220 | SM Building | 8.5 | 1.3 | 1 | 1 | 510731 | 1 | Active | 1306 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 256 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 2007 | 20 | 2027 | 2024 | 2026-02-15 | 5 - Very Poor | The wayfinding signage has aged and exceeded its EUL, lifecycle replacement is recommended. | 37964 | SM Building | 8.5 | 1.3 | 1 | 1 | 419502.2 | 1 | Active | 1332 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 48 | Soffit - Plaster on Metal Lath | B201008 | Exterior Soffits | The building's overhang soffits are plaster-on-metal lath. | 2007 | 50 | 2057 | 2037 | 2025-06-25 | 1 - Very Good | The exterior soffit is in good condition overall, no deficiencies were observed. | 2217 | SM | 169.94 | 1.3 | 1 | 1 | 489784.07 | 1 | Active | 1316 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 568 | Split DX Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | Cooling for the fish lab is provided by a Mitsubishi, cooling unit rated 6 tons. | 2008 | 18 | 2026 | 2026 | 2024-06-23 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 6 | Each | 5488.32 | 1.3 | 1 | 1 | 42808.9 | 1 | Active | 1310 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 571 | Split System A/C Unit | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | A 7.5-ton, split system, LIEBERT, air conditioning unit serves the NMR room. | 2012 | 18 | 2030 | 2027 | 2024-12-25 | 4 - Poor | No significant deficiencies were observed. | 8 | Each | 5488.32 | 1.3 | 1 | 1 | 57078.53 | 1 | Active | 1287 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 514 | Sump Pump - Submersible - 1/2 HP | D203001 | Sanitary Waste and Vent Piping and Fittings | The water drainage system includes a duplex stormwater sump pump system.. | 2007 | 50 | 2057 | 2055 | 2026-03-23 | 1 - Very Good | No significant deficiencies were observed. | 7126 | SM Building | 54.76 | 1.3 | 1 | 1 | 507285.69 | 1 | Active | 1339 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 686 | Suppression System | D409099 | Other Fire Protection Systems | The NMR is equipped with a Novec 1230 clean agent fire suppression system (482 lb of Novec 1230). | 2012 | 20 | 2032 | 2025 | 2024-02-10 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Lump Sum | 11000 | 1.3 | 1 | 1 | 57200 | 1 | Active | 1290 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 746 | Transformer | D501026 | Grounding Methods | The building is equipped with a 300kVA, 600V - 208Y/120V, transformer. | 2008 | 50 | 2058 | 2048 | 2026-01-11 | 1 - Very Good | No significant deficiencies were observed. | 4 | Each | 13719.68 | 1.3 | 1 | 1 | 71342.34 | 1 | Active | 1299 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 748 | Transformer - 225 KVA | D501026 | Grounding Methods | The building is equipped with a 225 KVA, 600V - 208Y/120V transformer that serves the Laboratory. | 2008 | 50 | 2058 | 2048 | 2026-01-13 | 1 - Very Good | No significant deficiencies were observed. | 3 | Each | 13719.68 | 1.3 | 1 | 1 | 53506.75 | 1 | Active | 1334 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 733 | Transformer - 75 KVA | D501026 | Grounding Methods | The building is equipped with three 75 KVA, 600V - 208Y/120V transformers. | 2007 | 50 | 2057 | 2026 | 2024-06-18 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 13719.68 | 1.3 | 1 | 1 | 53506.75 | 1 | Active | 1303 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 742 | Transformer - 75 KVA | D501026 | Grounding Methods | The building is equipped with three 75kVA, 600V - 208Y/120V, dry type transformers. | 2007 | 50 | 2057 | 2047 | 2025-11-04 | 1 - Very Good | No significant deficiencies were observed. | 3 | Each | 13719.68 | 1.3 | 1 | 1 | 53506.75 | 1 | Active | 1351 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 747 | Transformers - 75 KVA | D501026 | Grounding Methods | The building is equipped with a 75 KVA, 600Y - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2026-01-12 | 1 - Very Good | No significant deficiencies were observed. | 3 | Each | 13719.68 | 1.3 | 1 | 1 | 53506.75 | 1 | Active | 1330 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 749 | Transformers - 75 KVA | D501026 | Grounding Methods | The building is equipped with a 75 KVA, 600V - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2026-01-14 | 1 - Very Good | No significant deficiencies were observed. | 3 | Each | 13719.68 | 1.3 | 1 | 1 | 53506.75 | 1 | Active | 1335 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 734 | Transformers - 75 KVA - 1972 | D501026 | Grounding Methods | The building is equipped with a 75 KVA, 600V - 208Y/120V transformer on each floor. | 2007 | 50 | 2057 | 2026 | 2024-06-28 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 13719.68 | 1.3 | 1 | 1 | 53506.75 | 1 | Active | 1320 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 750 | Transformers - 75 KVA - 2008 | D501026 | Grounding Methods | The building is equipped with a 75 KVA, 600V - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2026-01-15 | 1 - Very Good | No significant deficiencies were observed. | 3 | Each | 13719.68 | 1.3 | 1 | 1 | 53506.75 | 1 | Active | 1361 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 641 | Unit Heaters - Hot Water | D305002 | Unit Heaters (Hydronic) | Heating for the mechanical penthouse and basement mechanical rooms is provided by suspended, forced hot water, unit heaters. | 2007 | 30 | 2037 | 2027 | 2024-12-27 | 4 - Poor | No significant deficiencies were observed. | 9 | Each | 4300.8 | 1.3 | 1 | 1 | 50319.36 | 1 | Active | 1350 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 350 | Urethane Flooring | C302007 | Painted / Sealed Floor | The building’s floor finishes include Urethane flooring located in the animal and CL3 labs. | 2012 | 15 | 2027 | 2027 | 2024-12-24 | 4 - Poor | The floor finish is in good condition overall, no deficiencies were observed. | 10925 | SM | 50.98 | 1.3 | 1 | 1 | 724043.45 | 1 | Active | 1286 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 472 | Water Dist Complete - Backflow Preventer - 2012 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes two (2) 4 inch backflow preventer installed in 2012, one on each of the two parallel lines. | 2012 | 40 | 2052 | 2052 | 2026-02-04 | 1 - Very Good | No significant deficiencies were observed. | 6878 | SM Building | 48.15 | 1.3 | 1 | 1 | 430528.41 | 1 | Active | 1340 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 485 | Water Heater - Elec - Residential - 85 Gallon | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a RHEEM, 322 Liter (85 gal), electric, water heater rated at 15000 W. | 2010 | 20 | 2030 | 2026 | 2024-07-01 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 8232.48 | 1.3 | 1 | 1 | 42808.9 | 1 | Active | 1324 | Academic | East Campus | East
| 01.074 | 4 | Mayo Building | Edmonton | 307 | Wood panels | C301022 | Wood Wall Finish | The buildings wall finishes include wood panels provided on the 4th, 3rd and 2nd floors. | 2007 | 25 | 2032 | 2032 | 2025-03-17 | 2 - Good | The wall finishes are in good condition overall, no significant deficiencies were observed. | 1238 | SM | 169.94 | 1.3 | 1 | 1 | 273501.44 | 1 | Active | 1366 | Academic | East Campus | East
| 04.750 | 7 | Science | Hearst | 374 | Acoustic Tile Ceiling - Exposed T-bar | C303004 | Adhered Acoustic Tile Ceiling | Ceiling finishes located in some offices on the 400 floor level include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2005 | 30 | 2035 | 2030 | 2025-02-19 | 3 - Fair | The ceiling tiles are in fair condition overall. | 23142 | SM | 89.69 | 1.3 | 1.25 | 1 | 3372859.72 | 1 | Active | 1536 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 318 | C302002 - Terrazzo | C302002 | Terrazzo Floor | The building's floor finish includes asbestos containing vinyl tiles. | 2021 | 50 | 2071 | 2071 | 2026-03-02 | 1 - Very Good |  | 2294 | SM | 613.67 | 1.3 | 1.25 | 1.5 | 3431412.51 | 0 | Active | 1596 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 332 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the offices. | 2005 | 10 | 2015 | 2026 | 2024-09-25 | 4 - Poor | The carpet tiles are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 16146 | SM | 103.85 | 1.3 | 1.25 | 1 | 2724738.41 | 1 | Active | 1550 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 620 | Central AHU - 10000 CFM | D304041 | Air Handling Units - Modular - Up to 20,000 CFM | The HVAC system has a central Air Handling Unit with cooling coils and electric heating coils rated 10000 CFM. | 1990 | 30 | 2020 | 2026 | 2024-09-18 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 186359.15 | 1.3 | 1.25 | 1 | 302833.62 | 1 | Active | 1539 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 621 | Central AHU - 2000 CFM | D304041 | Air Handling Units - Modular - Up to 20,000 CFM | The HVAC system includes a central Air Handling Unit with cooling coils and electric heating coils rated 2000 CFM. | 1984 | 30 | 2014 | 2026 | 2024-09-19 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 186359.15 | 1.3 | 1.25 | 1 | 302833.62 | 1 | Active | 1540 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 598 | Chilled Water Distribution System | D304006 | Chilled Water Distribution Systems | The HVAC system is provided with a chilled water distribution system which includes distribution piping, valves and insulation. | 1994 | 45 | 2039 | 2039 | 2025-08-13 | 1 - Very Good | No significant deficiencies were observed. | 24111 | SM Building | 72.7 | 1.3 | 1.25 | 1 | 2848413.26 | 1 | Active | 1579 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 663 | DDC/Pneumatic System | D306006 | Direct Digital Control Systems | HVAC controls include a hybrid DDC/Pneumatic system with basic pc control, moderate sensor types and quantities, as well as pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2024-09-20 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 36.82 | 1.3 | 1.25 | 1 | 2140747.02 | 1 | Active | 1541 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 664 | DDC/Pneumatic System - Hybrid | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities; and includes pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2024-09-23 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SM Building | 36.82 | 1.3 | 1.25 | 1 | 2765458.15 | 1 | Active | 1547 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 665 | DDC/Pneumatic System - Hybrid | D306006 | Direct Digital Control Systems | HVAC controls consists of a hybrid DDC/Pneumatic system which includes basic pc control, moderate sensor types and quantities, pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2024-10-05 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SM Building | 36.82 | 1.3 | 1.25 | 1 | 2270882.71 | 1 | Active | 1569 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 707 | Distribution Equipment - Motor Control Centres | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system for the building includes a motor control centre for the supply and control of electrical power to HVAC equipment and other motor loads and air handing units and includes wire and conduit. | 1972 | 40 | 2012 | 2026 | 2024-09-28 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 142685.11 | 1.3 | 1.25 | 1 | 231863.3 | 1 | Active | 1558 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 708 | Distribution Switchboards, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system for the building includes essential and normal power switchboards, panelboards, feeders, vertical bus duct, wire, conduit and associated equipment. | 1972 | 40 | 2012 | 2026 | 2024-09-29 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 142685.11 | 1.3 | 1.25 | 1 | 231863.3 | 1 | Active | 1559 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 712 | Distribution Switchboards, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal power switchboards, panelboards, feeders, transformers, vertical bus duct, wire, conduit and associated equipment. | 1994 | 40 | 2034 | 2034 | 2025-05-08 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 142685.11 | 1.3 | 1.25 | 1 | 231863.3 | 1 | Active | 1580 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 713 | Distribution Switchboards, Panelboards, and Feeders - 1997 | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system for the 1997 section includes essential and normal switchboards, panelboards, feeders, vertical bus duct, wire, conduit and associated equipment. | 1997 | 40 | 2037 | 2037 | 2025-07-05 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 142685.11 | 1.3 | 1.25 | 1 | 231863.3 | 1 | Active | 1554 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 584 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers and VAV terminal boxes with reheat coils installed throughout the building. | 2007 | 50 | 2057 | 2047 | 2025-11-20 | 1 - Very Good | No significant deficiencies were observed. | 8296 | SM Building | 144.45 | 1.3 | 1.25 | 1 | 1947330.45 | 1 | Active | 1586 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 406 | Elevator - 2 Levels | D101003 | Freight Elevators - Up to 3 Floors (Hydraulic) | The conveying equipment includes a 510 Kg (1,122 LBS) elevator for 2 levels. | 2012 | 30 | 2042 | 2042 | 2025-09-12 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 196393.23 | 1.3 | 1.25 | 1 | 319139 | 1 | Active | 1593 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 862 | Emergency Battery Pack | D509003 | Emergency Lighting Systems | The building is provided with self-contained emergency battery packs and lights. | 2007 | 20 | 2027 | 2027 | 2025-01-04 | 4 - Poor | No significant deficiencies were observed. | 89297 | SM Building | 6.61 | 1.3 | 1.25 | 3 | 2877484.2 | 1 | Active | 1595 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 460 | Emergency Eyewash and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 25 | 2025 | 2026 | 2024-10-07 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 15 | per lavatory | 10976.65 | 1.3 | 1.25 | 1 | 267555.84 | 1 | Active | 1572 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 858 | Emergency Generator - 240kW | D509002 | Emergency Power Generator Systems - Up to 300kVA | The building is equipped with a 300kVA, 240kW, 600V, CATERPILLAR, natural gas, emergency generator which includes batteries, control panel, main breaker and feeder. | 2012 | 30 | 2042 | 2042 | 2025-09-09 | 1 - Very Good | No significant deficiencies were observed. | 300 | kVA | 589.4 | 1.3 | 1.25 | 1 | 287332.5 | 1 | Active | 1533 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 798 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and include single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2007 | 35 | 2042 | 2042 | 2025-09-11 | 1 - Very Good | No significant deficiencies were observed. | 1100 | SM | 275.68 | 1.3 | 1.25 | 5 | 2463890 | 1 | Active | 1592 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 94 | Exterior Storefront Door - Double Leaf | B203003 | Exterior - Revolving Doors | The exterior doors consist of glass metal framed double-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 1972 | 25 | 1997 | 2024 | 2023-12-06 | 5 - Very Poor | The exterior doors have aged and exceeded there EUL, lifecycle replacement is recommended. | 2 | Each | 135232.64 | 1.3 | 1.25 | 1 | 439506.08 | 1 | Active | 1534 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 95 | Exterior Storefront Door - Double Leaf | B203003 | Exterior - Revolving Doors | The exterior doors consist of hollow metal glazed double -doors mounted by butt hinges to metal or aluminum door frames. | 1972 | 25 | 1997 | 2024 | 2023-12-07 | 5 - Very Poor | The exterior doors have aged and are in poor condition, lifecycle replacement is recommended | 2 | Each | 135232.64 | 1.3 | 1.25 | 1 | 439506.08 | 2 | Active | 1543 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 92 | Exterior windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 2024 | 35 | 2059 | 2049 | 2026-01-21 | 1 - Very Good |  | 1210 | SM | 1387.83 | 1.3 | 1.25 | 1 | 2728820.74 | 1 | Active | 1597 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 806 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes pull stations at all exit doors, audio and visual alarms, smoke detectors and duct smoke detectors. | 2007 | 20 | 2027 | 2027 | 2025-01-02 | 4 - Poor | No significant deficiencies were observed. | 29762 | SM Building | 60.42 | 1.3 | 1.25 | 1 | 2922107.57 | 1 | Active | 1588 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 828 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system which includes a maim control panel in the electrical room, an annunciator panel in the lobby and a number of secondary control panels throughout the building. | 2014 | 20 | 2034 | 2034 | 2025-05-09 | 2 - Good | No significant deficiencies were observed. | 29762 | SM Building | 60.42 | 1.3 | 1.25 | 1 | 2922107.57 | 1 | Active | 1589 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 807 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes all conduit, wire, and connections to the main control panel, secondary panels, pull stations, audible and visual alarms, as well as smoke detectors. | 2007 | 20 | 2027 | 2027 | 2025-01-03 | 4 - Poor | No significant deficiencies were observed. | 29762 | SM Building | 60.42 | 1.3 | 1.25 | 1 | 2922107.57 | 1 | Active | 1590 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 185 | Glazed partitions | C101006 | Glazed Partitions | The building’s interior partitions include glazed partitions located in various locations throughout the building. | 2007 | 75 | 2082 | 2057 | 2023-12-29 | 1 - Very Good | The glazed partitions are in good condition overall, no major deficiencies were observed | 1830 | SM | 1104.6 | 1.3 | 1.25 | 1 | 3284804.25 | 0 | Active | 1594 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 698 | High Voltage Electrical Service - 15kV, 600A | D501021 | Low Voltage Electrical Service | The electrical distribution system for the building includes a 15kV, 600A, 3-Phase, switchgear assembly that includes incoming feeder and distribution feeders. | 1997 | 40 | 2037 | 2037 | 2025-07-06 | 1 - Very Good | No significant deficiencies were observed. | 37954 | SM Building | 36.82 | 1.3 | 1.25 | 1 | 2270882.71 | 1 | Active | 1570 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 407 | Hydraulic Freight Elevator | D101003 | Freight Elevators - Up to 3 Floors (Hydraulic) | The conveying equipment includes a 2-storey hydraulic freight elevator having a capacity of 1814 Kg (4000 lb ). | 2016 | 30 | 2046 | 2046 | 2025-10-16 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 196393.23 | 1.3 | 1.25 | 1 | 319139 | 1 | Active | 1566 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 403 | Hydraulic Passenger Elevator - 2-Storey | D101003 | Freight Elevators - Up to 3 Floors (Hydraulic) | The conveying equipment includes a 2 storey hydraulic passenger elevator with a capacity of 4000LB (1814Kg). | 1982 | 30 | 2012 | 2026 | 2024-10-06 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 196393.23 | 1.3 | 1.25 | 1 | 319139 | 1 | Active | 1571 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 404 | Hydraulic Passenger Elevator - 3-Story | D101003 | Freight Elevators - Up to 3 Floors (Hydraulic) | The conveying equipment includes a 1588Kg (,500LBS), 3-storey, hydraulic passenger elevator, manufactured by Hydraulic and rated at 40 HP. | 1997 | 30 | 2027 | 2027 | 2025-01-01 | 4 - Poor | No significant deficiencies were observed. | 1 | Each | 196393.23 | 1.3 | 1.25 | 1 | 319139 | 1 | Active | 1551 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 70 | Insulated Metal Paneled Walls | B201028 | Insulated Metal Sandwich Panels | The building envelope includes insulated metal panels on steel frame exterior walls. | 1994 | 40 | 2034 | 2034 | 2025-05-07 | 2 - Good | The metal panels are in good condition overall, no major deficiencies were observed. | 3272 | SM | 566.46 | 1.3 | 1.25 | 1 | 3011867.82 | 1 | Active | 1576 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 211 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 1972 | 40 | 2012 | 2026 | 2024-09-21 | 4 - Poor | The doors are functioning as intended, lifecycle replacement can be deferred. | 23 | Each | 2200 | 1.3 | 1.25 | 1 | 82225 | 1 | Active | 1544 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 212 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The interior doors include hollow metal double doors with vision panels. | 1972 | 40 | 2012 | 2026 | 2024-10-01 | 4 - Poor | The double doors are in fair condition overall, and are functioning as intended. Lifecycle replacement can be deferred. | 21 | Each | 2200 | 1.3 | 1.25 | 1 | 75075 | 1 | Active | 1564 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 136 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2018 | 28 | 2046 | 2025 | 2024-02-25 | 5 - Very Poor | The roof is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 7616 | SM | 283.23 | 1.3 | 1.25 | 1 | 3505254.48 | 1 | Active | 1577 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 415 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 1990 | 35 | 2025 | 2026 | 2024-10-08 | 4 - Poor | No significant deficiencies were observed. | 150 | Each | 1433.6 | 1.3 | 1.25 | 1 | 349440 | 1 | Active | 1573 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 41 | Mechanical Louvres | B201005 | Exterior Louvers and Screens | The building’s exterior wall includes mechanical louvers located at the North-west side of the building. | 2012 | 50 | 2062 | 2052 | 2026-02-05 | 1 - Very Good | No major deficiencies were observed or reported. | 1873 | SM | 802.49 | 1.3 | 1.25 | 1 | 2442478.63 | 1 | Active | 1532 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 540 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 1997 | 40 | 2037 | 2037 | 2025-07-04 | 1 - Very Good | No significant deficiencies were observed. | 50773 | SM | 24.55 | 1.3 | 1.25 | 1 | 2025525.37 | 1 | Active | 1553 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 379 | Painted Ceiling Finish | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling. | 2007 | 15 | 2022 | 2025 | 2024-02-26 | 5 - Very Poor | The painted ceiling finish is in good condition overall, no major deficiencies were observed or reported. Lifecycle replacement can be deferred. | 45208 | SM | 31.16 | 1.3 | 1.25 | 1 | 2289107.08 | 1 | Active | 1584 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 299 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, and Concrete Masonry walls. | 2010 | 10 | 2020 | 2026 | 2024-09-16 | 4 - Poor | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 37017 | SM Building | 50.04 | 1.3 | 1.25 | 1 | 3010037.36 | 1 | Active | 1535 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 300 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, and Concrete Masonry walls. | 2010 | 10 | 2020 | 2026 | 2024-10-02 | 4 - Poor | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 37964 | SM Building | 50.04 | 1.3 | 1.25 | 1 | 3087042.66 | 1 | Active | 1565 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 652 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2024-09-27 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 400 | Each | 430.08 | 1.3 | 1.25 | 1 | 279552 | 1 | Active | 1557 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 653 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2024-10-04 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 400 | Each | 430.08 | 1.3 | 1.25 | 1 | 279552 | 1 | Active | 1568 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 837 | Public Address System | D503004 | Public Address and Music Systems | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2000 | 15 | 2015 | 2026 | 2024-10-10 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SM Building | 24.55 | 1.3 | 1.25 | 1 | 2743932.02 | 1 | Active | 1575 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 522 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage consists of roof drains, interior piping and discharge by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2024-09-17 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 34.93 | 1.3 | 1.25 | 1 | 2030860.76 | 1 | Active | 1538 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 523 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2024-09-22 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SM Building | 34.93 | 1.3 | 1.25 | 1 | 2623504.98 | 1 | Active | 1546 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 524 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2024-10-03 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 37594 | SM Building | 34.93 | 1.3 | 1.25 | 1 | 2133882.43 | 1 | Active | 1567 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 503 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron, copper and PVC piping with gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2024-09-30 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SM Building | 54.76 | 1.3 | 1.25 | 1 | 2478855.15 | 1 | Active | 1561 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 509 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1994 | 50 | 2044 | 2044 | 2025-10-04 | 1 - Very Good | No significant deficiencies were observed. | 24111 | SM Building | 54.76 | 1.3 | 1.25 | 1 | 2145517.34 | 1 | Active | 1578 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 512 | Sanitary Waste - Gravity Discharge - 1997 | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1997 | 50 | 2047 | 2047 | 2025-11-17 | 1 - Very Good | No significant deficiencies were observed. | 22873 | SM Building | 54.76 | 1.3 | 1.25 | 1 | 2035353.91 | 1 | Active | 1552 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 808 | Security System - Card Access | D503001 | Fire Alarm Systems | This facility is provided with a card access security system to monitor strategic doors within the facility that consists of main control panel proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 20 | 2030 | 2030 | 2025-02-21 | 3 - Fair | No significant deficiencies were observed. | 24111 | SM Building | 60.42 | 1.3 | 1.25 | 1 | 2367278.26 | 1 | Active | 1581 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 853 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility utilizes a card access security system to monitor strategic doors within the facility that includes main control panel, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2025-02-20 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 102897.59 | 1.3 | 1.25 | 1 | 167208.58 | 1 | Active | 1555 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 854 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a card access which includes main control panel, door contacts, proximity card readers, keypads, mag locks, electronic strikes, conduit and wiring. | 2010 | 15 | 2025 | 2030 | 2025-02-22 | 3 - Fair | No significant deficiencies were observed. | 2 | Each | 102897.59 | 1.3 | 1.25 | 1 | 334417.17 | 1 | Active | 1591 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 129 | Single-Ply Membrane Roof Cover - Ballasted | B301023 | Conventional - Single Ply Membrane | The roof is protected with a single-ply ballasted EPDM membrane and rigid insulation board substrate. | 2000 | 20 | 2020 | 2026 | 2024-09-26 | 4 - Poor | The roof is in fair condition overall, lifecycle replacement can be deferred. | 6954 | SM | 226.58 | 1.3 | 1.25 | 1 | 2560410.65 | 1 | Active | 1556 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 78 | Stone Veneer Siding | B201099 | Other Exterior Walls | The exterior walls include areas that have stone veneer siding. | 2007 | 40 | 2047 | 2047 | 2025-11-19 | 1 - Very Good | The exterior wall finish is in good condition overall, no major deficiencies were observed | 25 | Lump Sum | 5500 | 1.3 | 1.25 | 1 | 223437.5 | 1 | Active | 1583 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 9 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade, 6-in. thick.The basement floor is constructed as a concrete slab-on-grade. | 2007 | 75 | 2082 | 2082 | 2023-11-14 | 1 - Very Good | No significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate | 18557 | SM Footprint | 85.91 | 1.3 | 1.25 | 1 | 2590626.79 | 0 | Active | 1582 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 14 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2025-11-15 | 1 - Very Good | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 14434 | SM Footprint | 85.91 | 1.3 | 1.25 | 1 | 2015040.53 | 1 | Active | 1542 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 16 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2025-11-18 | 1 - Very Good | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 16372 | SM Footprint | 85.91 | 1.3 | 1.25 | 1 | 2285592.6 | 1 | Active | 1563 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 15 | Structural Slab on Grade - 1972 | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2025-11-16 | 1 - Very Good | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 18299 | SM Footprint | 85.91 | 1.3 | 1.25 | 1 | 2554609.02 | 1 | Active | 1549 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 408 | Traction Passenger Elevator - 3 Floor | D101003 | Freight Elevators - Up to 3 Floors (Hydraulic) | The conveying equipment includes a three storey, traction geared, elevator rated 907Kg ( 2,000 LBS). | 1972 | 30 | 2002 | 2024 | 2026-03-16 | 5 - Very Poor | The elevator has been in service 17 years beyond its rated useful life. The staff has reported that spare parts are difficult to obtain. Replacement is recommended. | 1 | Each | 196393.23 | 1.3 | 1.25 | 1 | 319139 | 1 | Active | 1537 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 409 | Traction Passenger Elevator - 3 Floor | D101003 | Freight Elevators - Up to 3 Floors (Hydraulic) | The conveying equipment includes a 3-storey, traction geared, passenger elevator rated 907 Kg (2000LBS). | 1972 | 30 | 2002 | 2024 | 2026-03-17 | 5 - Very Poor | The elevator has been in service 17 years beyond its rated useful life. The staff has reported that replacement parts are difficult to obtain. Replacement is recommended. | 1 | Each | 196393.23 | 1.3 | 1.25 | 1 | 319139 | 1 | Active | 1545 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 740 | Transformer - 1000 KVA | D501026 | Grounding Methods | The building is equipped with a 1000KVA , 13.8kV - 600Y/347V, 3-Phase, transformer located in the Main Electrical Vault. | 2000 | 50 | 2050 | 2040 | 2025-08-23 | 1 - Very Good | No significant deficiencies were observed. | 14 | Each | 13719.68 | 1.3 | 1.25 | 1 | 312122.72 | 1 | Active | 1560 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 741 | Transformer - 1000 KVA | D501026 | Grounding Methods | The building is equipped with a 1000 KVA, 13.8kVA - 600Y/347V transformer located in the Main Electrical Vault. | 2000 | 50 | 2050 | 2040 | 2025-08-24 | 1 - Very Good | No significant deficiencies were observed. | 14 | Each | 13719.68 | 1.3 | 1.25 | 1 | 312122.72 | 1 | Active | 1562 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 738 | Transformers - 300 KVA & 225 KVA | D501026 | Grounding Methods | The electrical system is equipped with two 300 KVA, 600V - 208Y/120V transformers; and two 225 KVA, 600V - 208Y/120V transformers located in the Main Electrical Vault. | 1982 | 50 | 2032 | 2026 | 2024-10-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 14 | Each | 13719.68 | 1.3 | 1.25 | 1 | 312122.72 | 1 | Active | 1574 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 488 | Water Heater - Elec - 20 Gallon | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 76 Liter (20-gal), John Wood, electric, water heater rated at 1,500 W. | 2012 | 20 | 2032 | 2026 | 2024-10-11 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 8232.48 | 1.3 | 1.25 | 1 | 13377.78 | 1 | Active | 1585 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 671 | Wet Sprinkler System - 40 HP Fire Pump | D401002 | Sprinklers (Wet) | The fire protection systems include a 40 HP fire pump and fire pump control panel. | 2007 | 40 | 2047 | 2042 | 2025-09-10 | 1 - Very Good | No significant deficiencies were observed. | 22324 | SM Building | 66.09 | 1.3 | 1.25 | 1 | 2397513.89 | 1 | Active | 1587 | Academic | Hearst Campus | South
| 04.750 | 7 | Science | Hearst | 678 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection, distribution piping and shutoff valves. | 1972 | 40 | 2012 | 2026 | 2024-09-24 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SM Building | 32.1 | 1.3 | 1.25 | 1 | 2410950.75 | 1 | Active | 1548 | Academic | Hearst Campus | South
| 31.896 | 6 | Skytop Detector Building | Pembroke | 412 | Acid Resistant and Stainless Steel Sinks | D201004 | Sinks | Laboratories contain a mix of acid resistant or stainless steel sinks set in casework. | 2012 | 35 | 2047 | 2025 | 2024-02-22 | 5 - Very Poor | No significant deficiencies were observed. | 104 | Each | 1433.6 | 1.3 | 1.18 | 1 | 228710.81 | 1 | Active | 1471 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 372 | Acoustic Tile Ceiling - Exposed T-bar | C303004 | Adhered Acoustic Tile Ceiling | The predominant ceiling finish in the building is suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids. | 2011 | 30 | 2041 | 2026 | 2024-08-21 | 4 - Poor | The ceiling tiles are in good condition overall, no deficiencies were observed or reported. Lifecycle replacement can be deferred. | 13993 | SM | 89.69 | 1.3 | 1.18 | 1 | 1925219.35 | 1 | Active | 1476 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 191 | Aluminum Screens | C101028 | Interior Guardrails and Screens | Aluminum screens are provided in various places throughout the building. | 2012 | 50 | 2062 | 2062 | 2024-01-01 | 1 - Very Good | The screens are in good condition overall, no major deficiencies were observed. | 276 | LM | 653.07 | 1.3 | 1.18 | 1 | 276499.39 | 0 | Active | 1527 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 204 | Automatic Door Operators | C102007 | Automatic Door Openers | The building includes automatic door opening devices located in various locations throughout the building. | 2012 | 15 | 2027 | 2027 | 2024-12-29 | 4 - Poor | No major deficiencies were observed or reported. | 20 | Each | 8646.76 | 1.3 | 1.18 | 1 | 265282.6 | 1 | Active | 1468 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 894 | Bridge to Plaza Building | G203028 | Pedestrian Bridges | The bridge to the Plaza Building is a steel framed structure with composite steel deck and concrete floor and steel roof deck. Its exterior walls are comprised of four-sided structural silicone curtain wall with insulated glazing units. Its roof is comprised of built-up roofing with black rubberized flood coat and black aggregate surfacing system. It has metal panel soffits. It is finished with porcelain tile flooring and painted ceiling. Replacement costs are for interior finishes and roofing. | 2012 | 40 | 2052 | 2087 | 2026-04-18 | 1 - Very Good | The bridge is in good condition overall, no deficiencies were observed or reported. | 226 | SM | 4342.88 | 1.3 | 1.18 | 4 | 6022428.04 | 0 | Active | 1467 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 838 | Clock System | D503006 | Clock and Program Systems | The building is provided with a centralized automatic wireless clock system which includes single sided clocks and a main controller. | 2012 | 15 | 2027 | 2027 | 2024-12-31 | 4 - Poor | No significant deficiencies were observed. | 175990 | SM Building | 6.61 | 1.3 | 1.18 | 1 | 1784492.84 | 1 | Active | 1528 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 51 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The building's exterior wall includes split face concrete masonry wall with CMU backup. | 2011 | 75 | 2086 | 2069 | 2023-11-24 | 1 - Very Good | The exterior wall is in fair condition overall, no significant deficiencies were observed or reported. | 1615 | SM | 726.96 | 1.3 | 1.18 | 1 | 1800977.97 | 0 | Active | 1519 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 668 | DDC System | D306006 | Direct Digital Control Systems | HVAC controls include a JOHNSON CONTROLS, DDC control system for system optimization, moderate sensor types and quantities installed throughout the building. | 2011 | 20 | 2031 | 2030 | 2025-02-15 | 3 - Fair | No significant deficiencies were observed. | 31850 | SM Building | 36.82 | 1.3 | 1.18 | 1 | 1798947.88 | 1 | Active | 1495 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 661 | DDC/Pneumatic System - Hybrid | D306006 | Direct Digital Control Systems | HVAC controls include a Hybrid DDC /Pneumatic system for system optimization, basic pc control, moderate sensor types with pneumatic activation of control valves and dampers. | 2011 | 20 | 2031 | 2026 | 2024-09-01 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 31850 | SM Building | 36.82 | 1.3 | 1.18 | 1 | 1798947.88 | 1 | Active | 1496 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 662 | DDC/Pneumatic System - Hybrid - Average | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities including pneumatic activation of control valves and dampers. | 2011 | 20 | 2031 | 2026 | 2024-09-10 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SM Building | 36.82 | 1.3 | 1.18 | 1 | 1573415.73 | 1 | Active | 1509 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 701 | Distribution Equipment, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal panelboards, feeders, transformers and associated equipment. | 2011 | 40 | 2051 | 2025 | 2024-02-23 | 5 - Very Poor | No significant deficiencies were observed. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1484 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 709 | Distribution Equipment, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal panelboards, feeders, transformers and associated equipment, vertical bus duct, wire and conduit. | 2011 | 40 | 2051 | 2030 | 2025-02-14 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1488 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 715 | Distribution Equipment, Panelboards, and Feeders - 600Y/347V & 208Y/120V | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal panelboards, feeders, transformers and associated equipment, as well as vertical bus duct, wire and conduit. | 2011 | 40 | 2051 | 2047 | 2025-11-13 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1524 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 704 | Distribution Switchboards | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system is provided with distribution switchboards which include incoming feeders, distribution breakers and distribution feeders. | 2011 | 40 | 2051 | 2026 | 2024-09-13 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1529 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 703 | Distribution Switchboards, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal power switchboards, panelboards, feeders, transformers, vertical bus duct, wire, conduit and associated equipment. | 2011 | 40 | 2051 | 2026 | 2024-09-12 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1515 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 710 | Distribution Switchboards, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal switchboards, panelboards, feeders and associated equipment. | 2011 | 40 | 2051 | 2030 | 2025-02-16 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1510 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 702 | Distribution Switchboards, Panelboards and Feeders - 1972 | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system for the 1972 section includes essential and normal switchboards, panelboards, feeders, vertical bus duct, wire, conduit and associated equipment. | 2011 | 40 | 2051 | 2026 | 2024-09-02 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1497 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 711 | Distribution Switchboards, Panelboards, and Feeders - 600Y/347V & 208Y/120V | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal switchboards, panelboards, feeders, transformers, vertical bus duct, wire, conduit and associated equipment,. | 2011 | 40 | 2051 | 2030 | 2025-02-17 | 3 - Fair | No significant deficiencies were observed. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1514 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 697 | Distribution Switchgear - 15kV, 600A | D501021 | Low Voltage Electrical Service | The electrical distribution system for the building consists of a 15kV, 600A, 3-Phase, 3-bay, switchgear assembly and includes all associated feeds, conduit and wire. | 2011 | 40 | 2051 | 2037 | 2025-07-03 | 1 - Very Good | No significant deficiencies were observed. | 27857 | SM Building | 36.82 | 1.3 | 1.18 | 1 | 1573415.73 | 1 | Active | 1511 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 466 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4” main branch piping, water meter, valves, insulation and fittings. | 2011 | 40 | 2051 | 2034 | 2025-05-06 | 2 - Good | No significant deficiencies were observed. | 24111 | SM Building | 48.15 | 1.3 | 1.18 | 1 | 1780889.09 | 1 | Active | 1521 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 463 | Domestic Water Distribution - 1972 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4” for main branch piping, water meter, valves, insulation and fittings. | 2011 | 40 | 2051 | 2026 | 2024-09-08 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 25704 | SM Building | 48.15 | 1.3 | 1.18 | 1 | 1898551.42 | 1 | Active | 1507 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 467 | Domestic Water Distribution - 1997 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4” main branch piping, water meter, valves, insulation and fittings. | 2011 | 40 | 2051 | 2037 | 2025-07-02 | 1 - Very Good | No significant deficiencies were observed. | 22873 | SM Building | 48.15 | 1.3 | 1.18 | 1 | 1689447.81 | 1 | Active | 1494 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 392 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 2011 | 25 | 2036 | 2026 | 2024-08-26 | 4 - Poor | The ceiling finish is in fair condition overall, lifecycle replacement can be deferred. | 11044 | SM | 113.29 | 1.3 | 1.18 | 1 | 1919302.08 | 1 | Active | 1486 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 393 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 2011 | 25 | 2036 | 2026 | 2024-08-30 | 4 - Poor | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 11840 | SM | 113.29 | 1.3 | 1.18 | 1 | 2057636.42 | 1 | Active | 1492 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 394 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 2011 | 25 | 2036 | 2026 | 2024-09-07 | 4 - Poor | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 11421 | SM | 113.29 | 1.3 | 1.18 | 1 | 1984819.73 | 1 | Active | 1506 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 866 | Emergency Battery Packs and Lights | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights. | 2012 | 20 | 2032 | 2032 | 2025-03-20 | 2 - Good | No significant deficiencies were observed. | 175861 | SM Building | 6.61 | 1.3 | 1.18 | 1 | 1783184.82 | 1 | Active | 1473 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 459 | Emergency Eyewash Units and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency eyewash and showers stations installed throughout the building. | 2011 | 25 | 2036 | 2026 | 2024-09-04 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 12 | per lavatory | 10976.65 | 1.3 | 1.18 | 1 | 202058.17 | 1 | Active | 1502 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 349 | Epoxy Flooring | C302007 | Painted / Sealed Floor | The building's floor finishes include cement epoxy floor finish located located in the laboratories on the 400 floor level. | 2011 | 15 | 2026 | 2026 | 2024-08-23 | 4 - Poor | The epoxy floor finish is in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 23142 | SM | 50.98 | 1.3 | 1.18 | 1 | 1809781.23 | 1 | Active | 1480 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 793 | Exit Signs | D502022 | Interior Lighting Systems (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2011 | 35 | 2046 | 2033 | 2025-04-14 | 2 - Good | No significant deficiencies were observed. | 4000 | SM | 275.68 | 1.3 | 1.18 | 1 | 1691572.48 | 1 | Active | 1477 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 121 | Exterior Storefront Door - Single Leaf | B203025 | Exterior Doors - Aluminum and Glass | The exterior doors consist of glazed metal framed single-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 2011 | 35 | 2046 | 2032 | 2025-03-21 | 2 - Good | The exterior doors are in good condition overall. | 8 | Each | 8838.66 | 1.3 | 1.18 | 1 | 108468.04 | 1 | Active | 1522 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 822 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building includes a fire alarm system that includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2025-04-30 | 2 - Good | No significant deficiencies were observed. | 21237 | SM Building | 60.42 | 1.3 | 1.18 | 1 | 1968336.05 | 1 | Active | 1498 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 825 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. | 2014 | 20 | 2034 | 2034 | 2025-05-03 | 2 - Good | No significant deficiencies were observed. | 22927 | SM Building | 60.42 | 1.3 | 1.18 | 1 | 2124972.49 | 1 | Active | 1516 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 823 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system that includes a main control panel, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2025-05-01 | 2 - Good | No significant deficiencies were observed. | 21237 | SM Building | 60.42 | 1.3 | 1.18 | 1 | 1968336.05 | 1 | Active | 1499 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 826 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes a maim fire alarm control panel, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2025-05-04 | 2 - Good | No significant deficiencies were observed. | 22927 | SM Building | 60.42 | 1.3 | 1.18 | 1 | 2124972.49 | 1 | Active | 1517 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 824 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes all conduit, wire, and connections to the control panels, pull stations, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2025-05-02 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 21237 | SM Building | 60.42 | 1.3 | 1.18 | 1 | 1968336.05 | 1 | Active | 1500 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 827 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes conduit, wire, and connections to the control panel, annunciator panel, pull stations, audio alarms, visual strobes and smoke detectors. | 2014 | 20 | 2034 | 2034 | 2025-05-05 | 2 - Good | No significant deficiencies were observed. | 22927 | SM Building | 60.42 | 1.3 | 1.18 | 1 | 2124972.49 | 1 | Active | 1518 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 22 | Foundation Wall and Footings - 12-ft. - Full Basement | A202002 | Basement Walls | The building is a three -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 2011 | 75 | 2086 | 2047 | 2025-11-10 | 1 - Very Good | No significant deficiencies were observed or reported. | 8268 | SM Footprint | 457.89 | 1.3 | 1.18 | 1 | 5807470.15 | 1 | Active | 1485 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 385 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include GWB ceiling located in the corridors. | 2011 | 15 | 2026 | 2026 | 2024-08-24 | 4 - Poor | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 37017 | SM | 31.16 | 1.3 | 1.18 | 1 | 1769391.87 | 1 | Active | 1481 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 386 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 2011 | 15 | 2026 | 2026 | 2024-08-31 | 4 - Poor | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 39827 | SM | 31.16 | 1.3 | 1.18 | 1 | 1903708.3 | 1 | Active | 1493 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 210 | Hollow Metal Single Doors | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 2011 | 40 | 2051 | 2026 | 2024-09-03 | 4 - Poor | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 37 | Each | 2200 | 1.3 | 1.18 | 1 | 124867.6 | 1 | Active | 1501 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 209 | Interior Hollow Metal Swing Doors - Double Leaf | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 2011 | 40 | 2051 | 2026 | 2024-08-29 | 4 - Poor | The doors are functioning as intended, lifecycle replacement can be deferred. | 14 | Each | 2200 | 1.3 | 1.18 | 1 | 47247.2 | 1 | Active | 1491 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 208 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The interior doors include hollow metal double doors with vision panels. | 2011 | 40 | 2051 | 2026 | 2024-08-22 | 4 - Poor | The double doors are in good condition overall, and are functioning as intended. Lifecycle replacement can be deferred. | 13 | Each | 2200 | 1.3 | 1.18 | 1 | 43872.4 | 1 | Active | 1479 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 222 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors include hollow metal double doors, hinge mounted on metal door frames. | 2011 | 40 | 2051 | 2038 | 2025-08-05 | 1 - Very Good | The interior double doors are in good condition overall, no deficiencies were observed. | 16 | Each | 2200 | 1.3 | 1.18 | 1 | 53996.8 | 1 | Active | 1474 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 182 | Interior Windows - Metal | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 200 floor level. | 2011 | 75 | 2086 | 2026 | 2024-08-28 | 4 - Poor | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 1884 | SM | 793.05 | 1.3 | 1.18 | 1 | 2291958.91 | 1 | Active | 1490 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 535 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes an acid water waste system which consists of glass piping for the laboratories. | 2011 | 30 | 2041 | 2040 | 2025-08-22 | 1 - Very Good | No significant deficiencies were observed. | 10764 | SM | 96.3 | 1.3 | 1.18 | 1 | 1590103.29 | 1 | Active | 1487 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 705 | Main Distribution Switchboard | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system is provided with a 1000A, 600Y/347V, 3-Phase, 4-Wire, Main Breaker Distribution Switchboard which includes incoming feeder, main breaker, distribution breakers and distribution feeders. | 2011 | 40 | 2051 | 2026 | 2024-09-14 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1530 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 706 | Main Distribution Switchboard | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system for the building is provided with a 3000A, 600V, 3-Phase, 4-Wire, Main Breaker Switchboard which includes incoming feeder, main breaker, distribution feeders and distribution feeders. | 2011 | 40 | 2051 | 2026 | 2024-09-15 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1531 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 716 | Main Distribution Switchboard - 600/347V-1200 A | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system is provided with a 600Y/347V, 3-Phase, 4-Wire, 1200A, Cutler-Hammer, main disconnect switchboard, SWBD-BB, which includes incoming feeder, distribution breakers and distribution feeders. | 2011 | 40 | 2051 | 2047 | 2025-11-14 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 142685.11 | 1.3 | 1.18 | 1 | 218878.96 | 1 | Active | 1525 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 402 | Metal Panel Ceiling | C303008 | Metal Ceiling | The building’s ceiling finishes include metal panel acoustic ceiling tiles. | 2012 | 40 | 2052 | 2042 | 2025-09-08 | 1 - Very Good | No major deficiencies were observed or reported. | 10118 | SM | 151.06 | 1.3 | 1.18 | 1 | 2344604.07 | 1 | Active | 1470 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 544 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 2011 | 40 | 2051 | 2040 | 2025-08-21 | 1 - Very Good | No significant deficiencies were observed. | 35779 | SM | 24.55 | 1.3 | 1.18 | 1 | 1347426.41 | 1 | Active | 1482 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 293 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2011 | 10 | 2021 | 2025 | 2024-02-24 | 5 - Very Poor | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 22991 | SM Building | 50.04 | 1.3 | 1.18 | 1 | 1764820.43 | 1 | Active | 1520 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 297 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB and CMU walls. | 2012 | 10 | 2022 | 2026 | 2024-08-20 | 4 - Poor | The painted wall finish is in good condition overall, no major deficiencies were observed. Lifecycle replacement can be deferred. | 25855 | SM Building | 50.04 | 1.3 | 1.18 | 1 | 1984664.96 | 1 | Active | 1475 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 298 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2011 | 10 | 2021 | 2026 | 2024-09-06 | 4 - Poor | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 27857 | SM Building | 50.04 | 1.3 | 1.18 | 1 | 2138341.21 | 1 | Active | 1505 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 61 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 level include sections of precast concrete panels. | 2011 | 75 | 2086 | 2047 | 2025-11-12 | 1 - Very Good | The exterior wall system is a fair condition overall, no significant deficiencies were observed. | 1399 | SM | 830.81 | 1.3 | 1.18 | 1 | 1782973.09 | 1 | Active | 1512 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 836 | Public Address System | D503004 | Public Address and Music Systems | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2011 | 15 | 2026 | 2026 | 2024-08-27 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SM Building | 24.55 | 1.3 | 1.18 | 1 | 1740631.33 | 1 | Active | 1489 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 521 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 2011 | 50 | 2061 | 2026 | 2024-09-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SM Building | 34.93 | 1.3 | 1.18 | 1 | 1492651.05 | 1 | Active | 1508 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 502 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building is provided with a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 2011 | 50 | 2061 | 2026 | 2024-09-05 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SM Building | 54.76 | 1.3 | 1.18 | 1 | 1617623.43 | 1 | Active | 1503 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 351 | Sealed Concrete Floor | C302007 | Painted / Sealed Floor | The buildings floor finishes include sealed concrete floor finish located in the mechanical rooms. | 2012 | 15 | 2027 | 2027 | 2024-12-30 | 4 - Poor | The sealed concrete floor finish is in poor condition, lifecycle replacement is recommended. | 22581 | SM | 50.98 | 1.3 | 1.18 | 1 | 1765909.17 | 1 | Active | 1469 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 844 | Security System - CCTV | D503008 | Intrusion Alarm Systems | The building is provided with a CCTV security system that monitors points of egress and includes video recorder, monitoring station, cameras, conduit and cabling. | 2011 | 20 | 2031 | 2030 | 2025-02-18 | 3 - Fair | No significant deficiencies were observed. | 89297 | SM Building | 12.27 | 1.3 | 1.18 | 1 | 1680764.21 | 1 | Active | 1526 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 12 | Structural Slab on Grade | A103001 | Slab on Grade | The building's substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 2011 | 75 | 2086 | 2047 | 2025-11-09 | 1 - Very Good | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 11324 | SM Footprint | 85.91 | 1.3 | 1.18 | 1 | 1492343.98 | 1 | Active | 1478 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 13 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 2011 | 75 | 2086 | 2047 | 2025-11-11 | 1 - Very Good | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 11421 | SM Footprint | 85.91 | 1.3 | 1.18 | 1 | 1505127.22 | 1 | Active | 1504 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 271 | Universal Washrooms | C104022 | Universal / Gender Neutral Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal partitions, as well as standard accessories. The washrooms are finished with ceramic floor and wall tiles and painted GWB ceiling finish. The fixtures include floor-mounted water closets and counter top lavatory sinks. | 2011 | 25 | 2036 | 2032 | 2025-03-22 | 2 - Good | The washrooms are in good condition overall, no major deficiencies were observed or reported. | 4 | Per Washroom | 15803.48 | 1.3 | 1.18 | 1 | 96970.15 | 1 | Active | 1523 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 870 | Vaccuum Pumps | E102002 | Vacuum Pumps | Vacuum pumps consist of four 7.5HP (40cfm) pumps | 2012 | 20 | 2032 | 2037 | 2025-07-01 | 1 - Very Good | No significant deficiencies were observed. | 4 | Each | 27439.36 | 1.3 | 1.18 | 1 | 168367.91 | 1 | Active | 1472 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 676 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet standpipe system with distribution piping and shutoff valves. | 2011 | 40 | 2051 | 2026 | 2024-08-25 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 32.1 | 1.3 | 1.18 | 1 | 1761808.05 | 1 | Active | 1483 | Academic | Northeast Campus | East
| 31.896 | 6 | Skytop Detector Building | Pembroke | 677 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with distribution piping and shutoff valves. | 2011 | 40 | 2051 | 2026 | 2024-09-11 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SM Building | 32.1 | 1.3 | 1.18 | 1 | 1868908.1 | 1 | Active | 1513 | Academic | Northeast Campus | East
| 03.521 | 8 | Sports and Health Ctr | Toronto | 376 | Acoustic Tile Ceiling - Exposed T-bar - 1972 | C303004 | Adhered Acoustic Tile Ceiling | The building's ceiling finishes include acoustic ceiling tiles with T-bar suspension system. | 1972 | 30 | 2002 | 2024 | 2026-03-13 | 5 - Very Poor | The ceiling tiles are in poor condition, lifecycle replacement is recommended. | 25511 | SM | 89.69 | 1.3 | 1.05 | 1 | 3123231.37 | 1 | Active | 1622 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 754 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring Systems | Branch wiring for the building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 50 | 2022 | 2026 | 2024-10-20 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SM Building | 114.24 | 1.3 | 1.05 | 1 | 3002890.36 | 1 | Active | 1634 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 761 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring Systems | Branch wiring for this building includes interior and exterior branch wiring, devices, and utilization equipment. | 1994 | 50 | 2044 | 2034 | 2025-05-11 | 2 - Good | No significant deficiencies were observed. | 24111 | SM Building | 114.24 | 1.3 | 1.05 | 1 | 3759811.47 | 1 | Active | 1660 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 762 | Branch Wiring - Equipment & Devices - Average Density - 1997 | D502001 | Branch Wiring Systems | Branch wiring for the 1997 section of the building includes interior and exterior branch wiring, devices and utilization equipment. | 1997 | 50 | 2047 | 2037 | 2025-07-09 | 1 - Very Good | No significant deficiencies were observed. | 22873 | SM Building | 114.24 | 1.3 | 1.05 | 1 | 3566760.72 | 1 | Active | 1627 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 313 | Ceramic Tile Flooring | C302001 | Ceramic Tile Floor | The building's floor finishes include ceramic floor tiles located in the lobby and the main entrance vestibules. | 1998 | 40 | 2038 | 2028 | 2025-01-17 | 3 - Fair | The ceramic tiles are in good condition overall, no significant deficiencies were observed or reported. | 15070 | SM | 217.14 | 1.3 | 1.05 | 1 | 4466689.23 | 1 | Active | 1610 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 596 | Chilled Water Piping | D304006 | Chilled Water Distribution Systems | The building is provided with chilled water piping and pumps. | 1972 | 45 | 2017 | 2026 | 2024-11-02 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SM Building | 72.7 | 1.3 | 1.05 | 1 | 3766384.17 | 1 | Active | 1669 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 556 | Chiller - Reciprocating | D303003 | Water Cooled Chillers | Cooling medium is provided by a Trane, reciprocating, air cooled, chiller with a cooling capacity of approximately 140 tons. | 2007 | 30 | 2037 | 2032 | 2025-03-25 | 2 - Good | No significant deficiencies were observed. | 140 | Ton | 1377.45 | 1.3 | 1.05 | 1 | 263230.7 | 1 | Active | 1663 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 262 | Communal Washroom | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 2005 | 25 | 2030 | 2030 | 2025-02-25 | 3 - Fair | The washrooms are in fair condition overall. | 6 | Per Lavatory | 21334.7 | 1.3 | 1.05 | 1 | 174731.19 | 1 | Active | 1638 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 261 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish. The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 2018 | 25 | 2043 | 2030 | 2025-02-23 | 3 - Fair | The washrooms are in good condition overall, no significant deficiencies were observed. | 8 | Per Lavatory | 21334.7 | 1.3 | 1.05 | 1 | 232974.92 | 1 | Active | 1632 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 263 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and counter top lavatory sinks. | 1982 | 25 | 2007 | 2030 | 2025-02-26 | 3 - Fair | The washrooms have aged and are in poor condition overall, lifecycle replacement is recommended. | 8 | Per Lavatory | 21334.7 | 1.3 | 1.05 | 1 | 232974.92 | 1 | Active | 1646 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 268 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish. The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 1972 | 25 | 1997 | 2024 | 2026-02-18 | 5 - Very Poor | The washrooms have aged and are in poor condition overall, lifecycle replacement is recommended. | 6 | Per Lavatory | 21334.7 | 1.3 | 1.05 | 1 | 174731.19 | 1 | Active | 1616 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 269 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 1972 | 25 | 1997 | 2024 | 2026-02-19 | 5 - Very Poor | The washrooms have aged and are in poor condition, lifecycle replacement is recommended. | 8 | Per Lavatory | 21334.7 | 1.3 | 1.05 | 1 | 232974.92 | 1 | Active | 1620 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 54 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior envelope of the building includes split face concrete masonry walls with CMU back-up. | 1972 | 75 | 2047 | 2047 | 2025-11-25 | 1 - Very Good | The exterior wall is in fair condition overall, no significant deficiencies were observed or reported. | 3767 | SM | 726.96 | 1.3 | 1.05 | 1 | 3737995.61 | 1 | Active | 1641 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 159 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) painted concrete masonry walls. | 1998 | 75 | 2073 | 2073 | 2023-12-19 | 1 - Very Good | The CMU partitions are in good condition overall, no deficiencies were observed. | 25855 | SM Building | 198.26 | 1.3 | 1.05 | 1 | 6997006.79 | 0 | Active | 1608 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 165 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2025-11-23 | 1 - Very Good | The interior walls are in good condition overall, no significant deficiencies were observed or reported. | 19267 | SM Building | 198.26 | 1.3 | 1.05 | 1 | 5214129.95 | 1 | Active | 1630 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 666 | DDC/Pneumatic System - Hybrid | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities with pneumatic activation of control valves and dampers. | 1982 | 20 | 2002 | 2026 | 2024-10-29 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SM Building | 36.82 | 1.3 | 1.05 | 1 | 3456884.91 | 1 | Active | 1650 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 695 | Distribution Switchgears - 15kV, 600A | D501021 | Low Voltage Electrical Service | The electrical distribution system for the building is provided with a 600A,15kV, switchgear which includes fused, 3-Pole, Kirk Inter-locked, interrupter switches and incoming feeder. | 1982 | 40 | 2022 | 2026 | 2024-10-31 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SM Building | 36.82 | 1.3 | 1.05 | 1 | 3456884.91 | 1 | Active | 1652 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 464 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building is provided with a water distribution system which includes a 4” main pipe, water meter, branch piping, valves, insulation and fittings. | 1972 | 40 | 2012 | 2026 | 2024-10-12 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 48.15 | 1.3 | 1.05 | 1 | 2351565.83 | 1 | Active | 1614 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 474 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4” for main pipe, backflow preventer, distribution piping, water meter, valves, insulation and fittings. | 2014 | 40 | 2054 | 2054 | 2026-03-19 | 1 - Very Good | No significant deficiencies were observed. | 46220 | SM Building | 48.15 | 1.3 | 1.05 | 1 | 3037797.95 | 1 | Active | 1618 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 476 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4” for main branch piping, water meter, valves, insulation and fittings. | 2015 | 40 | 2055 | 2055 | 2026-03-21 | 1 - Very Good | No significant deficiencies were observed. | 37594 | SM Building | 48.15 | 1.3 | 1.05 | 1 | 2470856.25 | 1 | Active | 1643 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 475 | Domestic Water Distribution - 2015 | D202001 | Domestic Water Piping and Fittings | The building is provided with a water distribution system which includes 4” main branch piping, water meter, valves, insulation and fittings. | 2015 | 40 | 2055 | 2055 | 2026-03-20 | 1 - Very Good | No significant deficiencies were observed. | 40828 | SM Building | 48.15 | 1.3 | 1.05 | 1 | 2683410.09 | 1 | Active | 1623 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 479 | Electric Water Heater - 2012 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a 27gal, electric, water heater, A.O Smith, model #: DEL 30 110. | 2014 | 20 | 2034 | 2025 | 2024-02-27 | 5 - Very Poor | No significant deficiencies were observed. Lifecycle replacement can be deferred. | 1 | Each | 8232.48 | 1.3 | 1.05 | 1 | 11237.34 | 1 | Active | 1602 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 444 | Emergency Eye Wash and Shower Stations | D201011 | Showers (Valve Set) | The plumbing fixtures include Emergency shower and eyewash stations. | 2012 | 25 | 2037 | 2037 | 2025-07-07 | 1 - Very Good | No significant deficiencies were observed. | 125 | Each | 2150.4 | 1.3 | 1.05 | 1 | 366912 | 1 | Active | 1601 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 572 | Evaporative Coolers | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | The HVAC system is provided with 30HP, rooftop, evaporative coolers | 2012 | 18 | 2030 | 2027 | 2025-01-05 | 4 - Poor | No significant deficiencies were observed. | 35 | Each | 5488.32 | 1.3 | 1.05 | 1 | 262204.49 | 1 | Active | 1603 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 85 | Exterior Windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1994 | 35 | 2029 | 2026 | 2024-11-01 | 4 - Poor | The windows are in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 1722 | SM | 1387.83 | 1.3 | 1.05 | 1 | 3262136.05 | 1 | Active | 1656 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 699 | Feeders | D501021 | Low Voltage Electrical Service | The electrical system is provided with two 500MCM, 15kV, feeders supplying a double-ended 600A 13.8kV switchgear with tie-breaker. One feeder is from the local municipal hydro, while the other feeder is from the CUB substation. | 2012 | 40 | 2052 | 2052 | 2026-04-08 | 1 - Very Good | No significant deficiencies were observed. | 58663 | SM Building | 36.82 | 1.3 | 1.05 | 1 | 2948361.32 | 1 | Active | 1605 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 248 | Fixed Casework - Lab Benches | C103011 | Millwork General | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1982 | 25 | 2007 | 2024 | 2026-02-11 | 5 - Very Poor | The fixed casework in the labs are in a very poor condition, lifecycle replacement is recommended. | 44315 | SM Building | 68.92 | 1.3 | 1.05 | 0.66 | 2751519.59 | 1 | Active | 1653 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 776 | Fluorescent Fixtures with T8 Lamps | D502002 | Interior Lighting Systems | Fluorescent fixtures with T8 lamps and electronic ballasts are provided in stairwells, service rooms and utility closets, etc. | 2012 | 35 | 2047 | 2042 | 2025-09-13 | 1 - Very Good | No significant deficiencies were observed. | 17578 | SM Building | 101.96 | 1.3 | 1.05 | 1 | 2446425.18 | 1 | Active | 1606 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 186 | Glazed partitions | C101006 | Glazed Partitions | The building’s interior partitions include glazed partitions located on the 4th and 5th floors. | 2012 | 75 | 2087 | 2062 | 2023-12-30 | 1 - Very Good | The glazed partitions are in good condition overall. | 2992 | SM | 1104.6 | 1.3 | 1.05 | 1 | 4511274.77 | 0 | Active | 1664 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 158 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1994 | 75 | 2069 | 2069 | 2023-12-18 | 1 - Very Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 24111 | SM Building | 198.26 | 1.3 | 1.05 | 1 | 6525036.96 | 0 | Active | 1657 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 160 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1998 | 75 | 2073 | 2073 | 2023-12-20 | 1 - Very Good | No significant deficiencies were observed. | 25855 | SM Building | 198.26 | 1.3 | 1.05 | 1 | 6997006.79 | 0 | Active | 1609 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 166 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1972 | 75 | 2047 | 2047 | 2025-11-24 | 1 - Very Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 19267 | SM Building | 198.26 | 1.3 | 1.05 | 1 | 5214129.95 | 1 | Active | 1631 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 608 | Heat Recovery Coils | D304025 | Heat Exchangers - Plate and Frame | The HVAC system is provided with Heat recovery coils. | 2012 | 30 | 2042 | 2037 | 2025-07-08 | 1 - Very Good | No significant deficiencies were observed. | 4 | Each | 18625.53 | 1.3 | 1.05 | 1 | 101695.39 | 1 | Active | 1604 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 591 | Heating Hot Water Distribution System | D304003 | Heating Water Distribution Systems | The HVAC system is rpovided with a heating hot water distribution system which includes distribution piping, valves and insulation. | 1994 | 45 | 2039 | 2039 | 2025-08-14 | 1 - Very Good | No significant deficiencies were observed. | 24111 | SM Building | 108.57 | 1.3 | 1.05 | 1 | 3573203.18 | 1 | Active | 1659 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 215 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The interior doors include hollow metal double doors with vision panels. | 1982 | 40 | 2022 | 2026 | 2024-10-26 | 4 - Poor | The interior doors are in a fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 24 | Each | 2200 | 1.3 | 1.05 | 1 | 72072 | 1 | Active | 1645 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 213 | Interior Hollow Metal Swing Doors - Single Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1972 | 40 | 2012 | 2026 | 2024-10-22 | 4 - Poor | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 75 | Each | 2200 | 1.3 | 1.05 | 1 | 225225 | 1 | Active | 1637 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 220 | Interior Hollow Metal Swing Doors - Single Leaf - Rated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1994 | 40 | 2034 | 2034 | 2025-05-10 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review. | 85 | Each | 2200 | 1.3 | 1.05 | 1 | 255255 | 1 | Active | 1658 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 178 | Interior Windows - Metal | C101005 | Interior Windows | The building includes windows installed in partition openings. | 2007 | 75 | 2082 | 2057 | 2023-12-27 | 1 - Very Good | The interior windows are in good condition overall, no deficiencies were observed. | 3122 | SM | 793.05 | 1.3 | 1.05 | 1 | 3379606.37 | 0 | Active | 1662 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 845 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System which includes main control panel, motion detectors, arming panels, wiring and conduit. | 2012 | 20 | 2032 | 2032 | 2025-03-26 | 2 - Good | No significant deficiencies were observed. | 175990 | SM Building | 12.27 | 1.3 | 1.05 | 1 | 2947577.31 | 1 | Active | 1665 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 140 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building's roof is an inverted roof membrane assembly with a ballasted built-up roof assembly system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2017 | 28 | 2045 | 2045 | 2025-10-14 | 1 - Very Good | The roof is in good condition overall, no major deficiencies were observed or reported. | 9235 | SM | 283.23 | 1.3 | 1.05 | 1 | 3570333.65 | 1 | Active | 1607 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 141 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof assembly system, where the built-up roof is insulated and protected by ballast. | 2017 | 28 | 2045 | 2045 | 2025-10-15 | 1 - Very Good | The roof is good condition overall, no deficiencies were observed. | 10473 | SM | 283.23 | 1.3 | 1.05 | 1 | 4048955.53 | 1 | Active | 1612 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 531 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes an acid waste water glass piping system for the laboratories. | 1984 | 30 | 2014 | 2026 | 2024-10-27 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 23681 | SM | 96.3 | 1.3 | 1.05 | 1 | 3112855.61 | 1 | Active | 1648 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 534 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes an acid water waste glass piping system for the laboratories. | 2000 | 30 | 2030 | 2030 | 2025-02-24 | 3 - Fair | No significant deficiencies were observed. | 19257 | SM | 96.3 | 1.3 | 1.05 | 1 | 2531323.02 | 1 | Active | 1633 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 770 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of wall mounted and recessed fluorescent fixtures with T- 8 lamps and electronic ballasts, conduit and wire. About 25% of the lamps are equipped with emergency power. | 2005 | 35 | 2040 | 2035 | 2025-06-02 | 2 - Good | No significant deficiencies were observed. | 24111 | SM Building | 101.96 | 1.3 | 1.05 | 1 | 3355658.07 | 1 | Active | 1661 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 775 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of recessed and surface mounted fluorescent fixtures with T-8 lamps and electronic ballasts including conduit and wire. About 25% of the lamps are equipped with emergency power. | 2010 | 35 | 2045 | 2040 | 2025-08-25 | 1 - Very Good | No significant deficiencies were observed. | 19257 | SM Building | 101.96 | 1.3 | 1.05 | 1 | 2680100.68 | 1 | Active | 1635 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 40 | Metal Wall Louvers | B201005 | Exterior Louvers and Screens | The building's exterior wall includes mechanical metal louvers located on the north side of the building. | 1972 | 50 | 2022 | 2026 | 2024-10-19 | 4 - Poor | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 2153 | SM | 802.49 | 1.3 | 1.05 | 1 | 2358393.72 | 1 | Active | 1629 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 724 | Motor Control Centres | D501024 | Main Service Panels | The electrical system is provided with motor control centres for the supply and control of electrical power to HVAC equipment and other motor loads. | 2012 | 40 | 2052 | 2052 | 2026-04-13 | 1 - Very Good | No significant deficiencies were observed. | 5 | Each | 17836.48 | 1.3 | 1.05 | 3 | 365201.93 | 1 | Active | 1667 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 301 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2010 | 10 | 2020 | 2026 | 2024-10-14 | 4 - Poor | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 46220 | SM Building | 50.04 | 1.3 | 1.05 | 1 | 3157038.61 | 1 | Active | 1617 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 302 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2005 | 10 | 2015 | 2026 | 2024-10-16 | 4 - Poor | The painted wall finish is in good condition overall. Lifecycle replacement can be deferred. | 63701 | SM Building | 50.04 | 1.3 | 1.05 | 1 | 4351071.32 | 1 | Active | 1621 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 654 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating in the washrooms and corridors. | 1982 | 18 | 2000 | 2026 | 2024-10-28 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 50 | Each | 430.08 | 1.3 | 1.05 | 10 | 293529.6 | 1 | Active | 1649 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 60 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 level includes sections of precast concrete panels. | 1994 | 75 | 2069 | 2069 | 2023-11-26 | 1 - Very Good | Efflorescences is observed on the concrete panels. Monitoring is recommended at this time. | 1938 | SM | 830.81 | 1.3 | 1.05 | 1 | 2197799.85 | 1 | Active | 1655 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 500 | Reverse Osmosis Water System | D202023 | Domestic Water Conditioners - Other | The labs are provided with two 60 gpm R.O. water systems. | 2012 | 20 | 2032 | 2032 | 2025-03-23 | 2 - Good | No significant deficiencies were observed. | 2 | Lump Sum | 11288.2 | 1.3 | 1.05 | 10 | 308167.86 | 1 | Active | 1600 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 125 | Roof Construction | B301021 | Conventional - Built-Up Roof | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1994 | 22 | 2016 | 2069 | 2023-12-10 | 1 - Very Good | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 2454 | SM | 245.47 | 1.3 | 1.05 | 1 | 822253.31 | 0 | Active | 1654 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 26 | Roof Deck - Metal Deck on Steel Frame | B103006 | Structural Steel Frame | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1972 | 75 | 2047 | 2047 | 2025-11-22 | 1 - Very Good | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 2086 | SM Building | 494.71 | 1.3 | 1.05 | 1 | 1408632.31 | 1 | Active | 1628 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 525 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1982 | 50 | 2032 | 2032 | 2025-03-24 | 2 - Good | No significant deficiencies were observed. | 68781 | SM Building | 34.93 | 1.3 | 1.05 | 1 | 3279440.25 | 1 | Active | 1647 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 527 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1997 | 50 | 2047 | 2047 | 2025-11-21 | 1 - Very Good | No significant deficiencies were observed. | 63701 | SM Building | 34.93 | 1.3 | 1.05 | 1 | 3037228.64 | 1 | Active | 1625 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 504 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building is provided with a sanitary waste system which consists of cast iron, copper and PVC piping, as well as gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2024-10-13 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 54.76 | 1.3 | 1.05 | 1 | 2674387.22 | 1 | Active | 1615 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 505 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building is provided with a sanitary waste system of cast iron, copper and PVC piping with gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2024-10-15 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SM Building | 54.76 | 1.3 | 1.05 | 1 | 3454824.83 | 1 | Active | 1619 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 507 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2024-10-25 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 37594 | SM Building | 54.76 | 1.3 | 1.05 | 1 | 2810053.76 | 1 | Active | 1644 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 506 | Sanitary Waste - Gravity Discharge - 1972 | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2024-10-17 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 40828 | SM Building | 54.76 | 1.3 | 1.05 | 1 | 3051786.85 | 1 | Active | 1624 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 214 | SIngle door | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1972 | 40 | 2012 | 2026 | 2024-10-24 | 4 - Poor | The interior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 59 | Each | 2200 | 1.3 | 1.05 | 1 | 177177 | 1 | Active | 1642 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 130 | Single-Ply Membrane Roof Cover - Ballasted | B301023 | Conventional - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2000 | 20 | 2020 | 2026 | 2024-10-21 | 4 - Poor | The roof is in a fair condition overall, lifecycle replacement can be deferred. | 10618 | SM | 226.58 | 1.3 | 1.05 | 1 | 3283953.09 | 1 | Active | 1636 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 229 | Solid Double Doors | C102008 | Interior Doors - Hollow Metal or Wood | The building includes hollow metal double doors with metal door frames. | 2012 | 40 | 2052 | 2052 | 2026-02-07 | 1 - Very Good | The interior doors are in good condition overall, no major deficiencies were observed. | 30 | Each | 2200 | 1.3 | 1.05 | 1 | 90090 | 1 | Active | 1599 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 228 | Solid Single Door | C102008 | Interior Doors - Hollow Metal or Wood | The building includes hollow metal and wood single doors attached to metal door frames. | 2012 | 40 | 2052 | 2052 | 2026-02-06 | 1 - Very Good | The single doors are in good condition overall. | 60 | Each | 2200 | 1.3 | 1.05 | 1 | 180180 | 1 | Active | 1598 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 868 | UPS System | D509007 | UPS Systems | The emergency power system is provided with a 240 kVA, APC, MGE GALAXY, UPS unit. | 2012 | 20 | 2032 | 2032 | 2025-03-27 | 2 - Good | No significant deficiencies were observed. | 240 | kVA | 1440.63 | 1.3 | 1.05 | 1 | 471950.39 | 1 | Active | 1666 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 361 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include vinyl floor tiles located in the labs and the hall ways. | 1998 | 15 | 2013 | 2025 | 2024-02-28 | 5 - Very Poor | The vinyl tiles are in a fair condition overall, lifecycle replacement can be deferred. | 17654 | SM | 119.6 | 1.3 | 1.05 | 1 | 2882086.12 | 1 | Active | 1611 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 370 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include asbestos containing vinyl floor tiles located in the laboratories and the corridors. | 1972 | 15 | 1987 | 2024 | 2026-03-10 | 5 - Very Poor | The vinyl tiles have aged significantly and are in poor condition overall. Life cycle replacement is recommended. Cost includes asbestos abatement. | 11926 | SM | 119.6 | 1.3 | 1.05 | 2 | 3893934.41 | 1 | Active | 1613 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 366 | Vinyl Tile Flooring - 1972 | C302022 | Vinyl Tile / Sheet Floor | The building's floor finish includes asbestos containing vinyl tiles. | 1972 | 15 | 1987 | 2026 | 2024-10-23 | 4 - Poor | The vinyl tiles are in fair condition overall, lifecycle replacement can be deferred. | 12317 | SM | 119.6 | 1.3 | 1.05 | 1.5 | 3016199.28 | 1 | Active | 1639 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 496 | Water Heater - 2015 - 105 L | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided from a 105 Liter, electric, water heater rated at 1500 W. | 2015 | 20 | 2035 | 2027 | 2025-01-06 | 4 - Poor | No significant deficiencies were observed. | 1 | Each | 8232.48 | 1.3 | 1.05 | 1 | 11237.34 | 1 | Active | 1640 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 497 | Water Heater - Elec- 105 Litres | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a RHEEM, 105-Litre, electric, water heater rated at 6,000 W. | 2015 | 20 | 2035 | 2027 | 2025-01-07 | 4 - Poor | No significant deficiencies were observed. | 1 | Each | 8232.48 | 1.3 | 1.05 | 1 | 11237.34 | 1 | Active | 1668 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 679 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a standpipe system which Includes distribution piping, fire hose and shutoff valves | 1972 | 40 | 2012 | 2026 | 2024-10-18 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 63701 | SM Building | 32.1 | 1.3 | 1.05 | 1 | 2791154.87 | 1 | Active | 1626 | Athletics | Downtown Campus | North
| 03.521 | 8 | Sports and Health Ctr | Toronto | 680 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system which Includes distribution piping and shutoff valves | 1982 | 40 | 2022 | 2026 | 2024-10-30 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SM Building | 32.1 | 1.3 | 1.05 | 1 | 3013742.69 | 1 | Active | 1651 | Athletics | Downtown Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 341 | Acid Resistant Sheet Vinyl | C302006 | Masonry and Stone Floor | The buildings floor finishes include acid resistant sheet vinyl. | 2012 | 50 | 2062 | 2027 | 2025-01-10 | 4 - Poor | The floor finish is in good condition overall, no major deficiencies were observed. | 5500 | SM | 849.69 | 1.3 | 1.15 | 1 | 6986576.03 | 1 | Active | 1735 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 396 | Acoustic Tile Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | Ceiling finishes located in offices, corridors and bookstore include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2007 | 25 | 2032 | 2027 | 2025-01-08 | 4 - Poor | The acoustic ceiling tiles in a good condition overall, no major deficiencies were observed. | 44089 | SM | 113.29 | 1.3 | 1.15 | 1 | 7467290 | 1 | Active | 1726 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 230 | Aluminim Doors | C102023 | Interior Doors - Aluminum and Glass | The building’s interior doors include glazed aluminum framed doors. | 2012 | 45 | 2057 | 2052 | 2026-02-08 | 1 - Very Good | The doors are in good condition overall, no major deficiencies were observed. | 46 | Each | 3273.58 | 1.3 | 1.15 | 1 | 225124.1 | 1 | Active | 1673 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 553 | Boiler HW - Gas-Fired | D302015 | Hot Water Boilers - Over 1000 MBH | Heating hot water is provided by two Viessmann Vitorono 200, gas-fired, hot water boilers, Boiler #1 & Boiler #2, each rated at 2031 MBH. | 2007 | 30 | 2037 | 2037 | 2025-07-13 | 1 - Very Good | No significant deficiencies were observed. | 4062 | MBH | 73.37 | 1.3 | 1.15 | 1 | 445553.27 | 1 | Active | 1729 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 755 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring Systems | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 2003 | 50 | 2053 | 2026 | 2024-11-07 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 114.24 | 1.3 | 1.15 | 1 | 6110652.48 | 1 | Active | 1687 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 756 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring Systems | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 2003 | 50 | 2053 | 2026 | 2024-11-12 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SM Building | 114.24 | 1.3 | 1.15 | 1 | 4757663.6 | 1 | Active | 1704 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 895 | Bridge to MC Building | G203028 | Pedestrian Bridges | The bridge to the MC Building is a steel framed structure with composite steel deck and concrete floor and steel roof deck. Its exterior walls are comprised of four-sided structural silicone curtain wall with insulated glazing units, some with fritted glass. Its roof is comprised of standing seam metal paneling. It has metal panel soffits. It is finished with resilient sheet flooring and metal panel ceiling. Replacement costs are for roofing and interior finishes. | 2012 | 40 | 2052 | 2087 | 2026-04-19 | 1 - Very Good | The bridge is in good condition overall, no deficiencies were observed or reported. | 1130 | SM | 4342.88 | 1.3 | 1.15 | 3 | 22009932.98 | 0 | Active | 1671 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 624 | Central AHU | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system serving both the C-Block and the F-Block includes a central AHU with chilled water coils, and electric heating elements having a approximate capacity of approximately 20,000 CFM. It branches off into two separate streams and is located in the basement of F-Block. | 2003 | 40 | 2043 | 2026 | 2024-11-10 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 358382.29 | 1.3 | 1.15 | 1 | 535781.52 | 1 | Active | 1702 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 628 | Central AHU - AHU-1 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system is provided with a 5,000 CFM central AHU that includes chilled water coils, hot water coils and steam humidification. | 2003 | 40 | 2043 | 2037 | 2025-07-12 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 358382.29 | 1.3 | 1.15 | 1 | 535781.52 | 1 | Active | 1709 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 629 | Central AHU - Air Handler - 12000 CFM- AHU-2 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system includes an ENG AIR, Air Handling Unit (AHU-2) with chilled water coils and hot water coils having a capacity of 12,000 CFM. | 2007 | 40 | 2047 | 2047 | 2025-12-07 | 1 - Very Good | No significant deficiencies were observed. | 1 | Each | 358382.29 | 1.3 | 1.15 | 1 | 535781.52 | 1 | Active | 1730 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 626 | Central AHU - Air Handler - 30000 CFM - HC-1 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system has a central AHU with chilled water coils and hot water coils having a approximate capacity of 30000 CFM. | 2003 | 40 | 2043 | 2026 | 2024-11-16 | 4 - Poor | No significant deficiencies were observed. | 1 | Each | 358382.29 | 1.3 | 1.15 | 1 | 535781.52 | 1 | Active | 1717 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 623 | Central AHU - Air Handler - Electric Heat - Serves Both B and E Blocks | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system serving both the B-Block and the E-Block includes a central AHU with chilled water coils, and heating hot water coils having a capacity of approximately 30000 CFM. It branches off into two separate streams and is located in the basement of E-Block. | 2003 | 40 | 2043 | 2026 | 2024-11-08 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 358382.29 | 1.3 | 1.15 | 1 | 535781.52 | 1 | Active | 1697 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 625 | Central AHU - D and G Blocks | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system includes a 20,000 cfm, central AHU with chilled water coils and electric heating elements that serves both the D-Block and the G-Block. It branches off into two separate streams and is located in the basement of F-Block. | 2003 | 40 | 2043 | 2026 | 2024-11-13 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 358382.29 | 1.3 | 1.15 | 1 | 535781.52 | 1 | Active | 1710 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 627 | Central Air Handling Unit | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system is provided with a 2,000 cfm, central Air Handling Unit (AHU) that includes chilled water coils, hot water coils and steam humidification. | 2003 | 40 | 2043 | 2034 | 2025-05-12 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 358382.29 | 1.3 | 1.15 | 1 | 535781.52 | 1 | Active | 1720 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 270 | Communal Washroom | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish. The fixtures include floor-mounted water closets, wall-mounted urinals, and counter top lavatory sinks. | 2003 | 25 | 2028 | 2024 | 2026-02-20 | 5 - Very Poor | The washrooms have aged and are in poor condition overall, lifecycle replacement is recommended. | 12 | Per Lavatory | 21334.7 | 1.3 | 1.15 | 1 | 382744.52 | 1 | Active | 1684 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 265 | Communal washrooms | C104021 | Communal Washroom Refurbishment | The communal washrooms have standard washroom fixtures and are finished with ceramic floor and wall tiles. The ceiling finish is painted precast ceiling. | 2007 | 25 | 2032 | 2032 | 2025-04-03 | 2 - Good | The washrooms are in a good condition overall | 10 | Per Lavatory | 21334.7 | 1.3 | 1.15 | 1 | 318953.77 | 1 | Active | 1742 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 55 | Concrete Masonry Unit Exterior Walls | B201021 | Masonry | The building's exterior wall system include painted concrete masonry walls. | 2003 | 75 | 2078 | 2047 | 2025-11-29 | 1 - Very Good | The exterior walls are in good condition overall, no significant deficiencies were observed or reported. | 5705 | SM | 726.96 | 1.3 | 1.15 | 1 | 6200223.67 | 1 | Active | 1689 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 56 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior wall includes split face concrete masonry walls. | 2003 | 75 | 2078 | 2047 | 2025-12-01 | 1 - Very Good | The exterior walls are in a fair condition overall, no significant deficiencies were observed. | 5059 | SM | 726.96 | 1.3 | 1.15 | 1 | 5498147.51 | 1 | Active | 1695 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 167 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) painted hollow concrete masonry walls. | 2003 | 75 | 2078 | 2047 | 2025-11-27 | 1 - Very Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 37017 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 10971790.68 | 1 | Active | 1680 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 169 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) concrete masonry walls. | 2003 | 75 | 2078 | 2047 | 2025-12-03 | 1 - Very Good | The interior walls are in good condition overall, no significant deficiencies were observed or reported. | 27857 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 8256778.59 | 1 | Active | 1699 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 171 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) painted hollow concrete masonry walls. | 2003 | 75 | 2078 | 2047 | 2025-12-05 | 1 - Very Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 37964 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 11252480.25 | 1 | Active | 1708 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 79 | Copper Clad Siding | B201099 | Other Exterior Walls | The exterior walls include areas that have copper cladding, waterproof membrane, fiberglass sheathed gypsum board, expanded polystyrene insulation, precast concrete panel on structural metal studs. | 2007 | 40 | 2047 | 2047 | 2025-12-06 | 1 - Very Good | No significant deficiencies were observed or reported. | 70 | Lump Sum | 5500 | 1.3 | 1.15 | 1 | 575575 | 1 | Active | 1722 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 667 | DDC System | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities. | 2007 | 20 | 2027 | 2027 | 2025-01-09 | 4 - Poor | No significant deficiencies were observed. | 89297 | SM Building | 36.82 | 1.3 | 1.15 | 1 | 4915433.73 | 1 | Active | 1732 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 465 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4” for main branch piping, water meter, valves, insulation and fittings. | 2003 | 40 | 2043 | 2026 | 2024-11-15 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 61903 | SM Building | 48.15 | 1.3 | 1.15 | 1 | 4456041.03 | 1 | Active | 1715 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 575 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system is provided with ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building.. | 2003 | 50 | 2053 | 2026 | 2024-11-09 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SM Building | 144.45 | 1.3 | 1.15 | 1 | 4158602.11 | 1 | Active | 1698 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 581 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal boxes installed throughout the building. | 2003 | 50 | 2053 | 2034 | 2025-05-13 | 2 - Good | No significant deficiencies were observed. | 24111 | SM Building | 144.45 | 1.3 | 1.15 | 1 | 5206836.76 | 1 | Active | 1721 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 582 | Ductwork Distribution System - 1997 | D304001 | Air Distribution Systems | The HVAC system for the1997 section of the building includes ductwork, dampers, diffusers and VAV terminal with hot water reheat coils. | 2003 | 50 | 2053 | 2037 | 2025-07-11 | 1 - Very Good | No significant deficiencies were observed. | 22873 | SM Building | 144.45 | 1.3 | 1.15 | 1 | 4939487.25 | 1 | Active | 1693 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 395 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Panel Ceiling | The building's ceiling finishes include egg crate ceiling tiles located in the offices. | 2003 | 25 | 2028 | 2026 | 2024-11-06 | 4 - Poor | The eggcrate ceiling is in good condition overall, no deficiencies were observed. lifecycle replacement can be deferred. | 37017 | SM | 113.29 | 1.3 | 1.15 | 1 | 6269515.62 | 1 | Active | 1685 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 618 | Exhaust System - Fume Hoods | D304031 | Exhaust Fans | The HVAC ventilation system for the labs includes constant volume fume hoods with exhaust systems. | 2003 | 25 | 2028 | 2026 | 2024-11-17 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 120 | Each | 4116.81 | 1.3 | 1.15 | 1 | 738555.71 | 1 | Active | 1718 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 81 | Exterior Windows | B202001 | Windows | The buildings exterior windows are aluminum framed with insulating glass. | 2003 | 35 | 2038 | 2024 | 2023-12-01 | 5 - Very Poor | The windows have aged but are in fair condition overall, lifecycle replacement can be deferred. | 3445 | SM | 1387.83 | 1.3 | 1.15 | 1 | 7147706.15 | 2 | Active | 1706 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 89 | Exterior windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 2003 | 35 | 2038 | 2028 | 2025-01-18 | 3 - Fair | The windows are in good condition overall, no significant deficiencies were observed. | 2400 | SM | 1387.83 | 1.3 | 1.15 | 1 | 4979534.04 | 1 | Active | 1677 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 882 | Fume Hoods | E102007 | Fume Hood Systems | The labs are provided with fume hoods, some of which have high-efficiency particulate arrestance or HEPA filters. | 2012 | 25 | 2037 | 2037 | 2025-07-10 | 1 - Very Good | No significant deficiencies were observed. | 73 | Each | 6859.84 | 1.3 | 1.15 | 1 | 748648.64 | 1 | Active | 1676 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 168 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's interior partitions include standard gypsum board partitions with painted finish. | 2003 | 75 | 2078 | 2047 | 2025-11-28 | 1 - Very Good | The interior partitions are in good condition overall, no significant deficiencies were observed. | 37017 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 10971790.68 | 1 | Active | 1681 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 170 | Gypsum Board Partitions - Metal Frame - 1972 | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 2003 | 75 | 2078 | 2047 | 2025-12-04 | 1 - Very Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 27857 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 8256778.59 | 1 | Active | 1700 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 588 | Heating Hot Water Piping | D304003 | Heating Water Distribution Systems | The HVAC system is provided with Heating Hot Water piping and pumps. | 2003 | 45 | 2048 | 2026 | 2024-11-22 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SM Building | 108.57 | 1.3 | 1.15 | 1 | 6160395.34 | 1 | Active | 1741 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 216 | Interior Hollow Metal Swing Doors - Single Leaf - Non rated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 2003 | 40 | 2043 | 2026 | 2024-11-05 | 4 - Poor | The interior doors are in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 120 | Each | 2200 | 1.3 | 1.15 | 1 | 394680 | 1 | Active | 1683 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 183 | Interior Windows - Metal | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 400 floor level. | 2003 | 75 | 2078 | 2026 | 2024-11-04 | 4 - Poor | No deficiencies were observed or reported. Lifecycle replacement can be deferred. | 4553 | SM | 793.05 | 1.3 | 1.15 | 1 | 5398081.19 | 1 | Active | 1682 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 839 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System which consists of main control panel, ultrasonic detection devices, arming panels, conduit and shielded wire. | 2009 | 20 | 2029 | 2029 | 2025-01-25 | 3 - Fair | No significant deficiencies were observed. | 269980 | SM Building | 12.27 | 1.3 | 1.15 | 1 | 4952418.63 | 1 | Active | 1737 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 137 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof membrane assembly (IRMA) consisting of ballast, filter fabric, extruded polystyrene insulation board, drainage mat and a fully adhered single-ply membrane | 2007 | 28 | 2035 | 2035 | 2025-06-03 | 2 - Good | According to information provided the roof is in good condition overall, no deficiencies were observed. | 18299 | SM | 283.23 | 1.3 | 1.15 | 1 | 7748324.53 | 1 | Active | 1724 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 138 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2013 | 28 | 2041 | 2041 | 2025-08-28 | 1 - Very Good | The roof is in good condition overall, no significant deficiencies were observed or reported. | 14176 | SM | 283.23 | 1.3 | 1.15 | 1 | 6002527.38 | 1 | Active | 1690 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 139 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2016 | 28 | 2044 | 2044 | 2025-10-05 | 1 - Very Good | The roof is in good condition overall, no significant deficiencies were observed or reported. | 16599 | SM | 283.23 | 1.3 | 1.15 | 1 | 7028495.48 | 1 | Active | 1692 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 536 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes an acid water waste glass piping system for the laboratories. | 2010 | 30 | 2040 | 2040 | 2025-08-26 | 1 - Very Good | No significant deficiencies were observed. | 35779 | SM | 96.3 | 1.3 | 1.15 | 1 | 5151048.96 | 1 | Active | 1686 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 537 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes a acid water waste glass piping system for the laboratories. | 2010 | 30 | 2040 | 2040 | 2025-08-27 | 1 - Very Good | No significant deficiencies were observed. | 27857 | SM | 96.3 | 1.3 | 1.15 | 1 | 4010530.5 | 1 | Active | 1701 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 766 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts, breakers, conduit and wire. About 25% of the lamps are equipped with emergency power. | 2003 | 35 | 2038 | 2025 | 2024-02-29 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 101.96 | 1.3 | 1.15 | 1 | 5453800.13 | 1 | Active | 1688 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 767 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts including conduit and wire. | 2003 | 35 | 2038 | 2026 | 2024-11-14 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 34428 | SM Building | 101.96 | 1.3 | 1.15 | 1 | 5247866.93 | 1 | Active | 1711 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 774 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts, breaker, conduit and wire. About 25% of the lamps are equipped with emergency power. | 2009 | 35 | 2044 | 2039 | 2025-08-15 | 1 - Very Good | No significant deficiencies were observed. | 27857 | SM Building | 101.96 | 1.3 | 1.15 | 1 | 4246248.08 | 1 | Active | 1705 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 291 | Painted Wall Finish - Masonry | C301005 | Painted Wall Covering | Standard paint finish is applied to the Concrete Masonry walls. | 2012 | 10 | 2022 | 2024 | 2024-01-03 | 5 - Very Poor | The painted wall finish is in poor condition, lifecycle replacement is recommended. | 68781 | SM Building | 50.04 | 1.3 | 1.15 | 1 | 5145492.85 | 1 | Active | 1714 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 294 | Painted Wall Surface | C301005 | Painted Wall Covering | The building's interior finishes include painted wall finish applied to GWB and CMU partitions. | 2015 | 10 | 2025 | 2025 | 2024-03-02 | 5 - Very Poor | The painted wall finish on the 3rd and 4th floor is in poor condition, repainting is recommended. | 85097 | SM Building | 50.04 | 1.3 | 1.15 | 1 | 6366089.55 | 1 | Active | 1725 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 411 | Passenger Elevators | D101004 | Wheelchair Lifts | The conveying equipment includes two 6-storey, 3000 LB (1361 Kg), passenger elevators. | 2007 | 25 | 2032 | 2032 | 2025-04-01 | 2 - Good | No significant deficiencies were observed. | 12 | Each | 43005.78 | 1.3 | 1.15 | 1 | 771523.69 | 1 | Active | 1727 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 644 | Perimeter Heat - Electric Baseboard | D305004 | Finned Tube Radiation Units | The HVAC equipment includes electric baseboard heating in the exterior offices. | 2007 | 30 | 2037 | 2026 | 2024-11-18 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 6000 | SM | 60.96 | 1.3 | 1.15 | 0.5 | 273405.6 | 1 | Active | 1731 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 655 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 2003 | 18 | 2021 | 2026 | 2024-11-11 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 1000 | Each | 430.08 | 1.3 | 1.15 | 1 | 642969.6 | 1 | Active | 1703 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 315 | Porcelain Tile | C302001 | Ceramic Tile Floor | The building’s floor finishes include porcelain floor tiles located on the 2nd and 3rd floor corridors. | 2012 | 40 | 2052 | 2042 | 2025-09-14 | 1 - Very Good | The floor tiles are in good condition overall, no major deficiencies were observed. | 18945 | SM | 217.14 | 1.3 | 1.15 | 1 | 6150007.36 | 1 | Active | 1674 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 62 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels with concrete masonry unit back-up. | 2005 | 75 | 2080 | 2047 | 2025-11-30 | 1 - Very Good | The precast concrete walls are in fair condition overall, no significant deficiencies were observed or reported. | 3983 | SM | 830.81 | 1.3 | 1.15 | 1 | 4947128.76 | 1 | Active | 1691 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 63 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels with concrete masonry unit back-up. | 2003 | 75 | 2078 | 2047 | 2025-12-02 | 1 - Very Good | Efflorescence was observed on the precast panels. A study is recommended to investigate the cause with a follow on major repair (based on the results of the study) to correct the issue. | 3337 | SM | 830.81 | 1.3 | 1.15 | 1 | 4144757.39 | 1 | Active | 1696 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 126 | Roof Construction | B301021 | Conventional - Built-Up Roof | Roof construction Is a reinforced concrete structure supported by CIP concrete columns. | 2012 | 22 | 2034 | 2087 | 2023-12-11 | 1 - Very Good | The roof construction is in good condition overall, no major deficiencies were observed. | 3385 | SM | 245.47 | 1.3 | 1.15 | 1 | 1242219.35 | 0 | Active | 1672 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 27 | Roof Deck - Metal Deck on Steel Frame | B103006 | Structural Steel Frame | The building's roof is a concrete infilled metal pan roof deck on open web steel joists | 2003 | 75 | 2078 | 2047 | 2025-11-26 | 1 - Very Good | The roof deck is in good condition overall, no significant deficiencies were observed or reported. | 3397 | SM Building | 494.71 | 1.3 | 1.15 | 1 | 2512392.16 | 1 | Active | 1679 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 529 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 2007 | 50 | 2057 | 2057 | 2026-03-26 | 1 - Very Good | No significant deficiencies were observed. | 89297 | SM Building | 34.93 | 1.3 | 1.15 | 1 | 4663120.59 | 0 | Active | 1728 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 508 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 2003 | 50 | 2053 | 2032 | 2025-03-31 | 2 - Good | No significant deficiencies were observed. | 68781 | SM Building | 54.76 | 1.3 | 1.15 | 1 | 5630839.1 | 1 | Active | 1716 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 856 | Security System - Card Access & CCTV | D503021 | Audio Visual Systems Theater | The building is provided with a Security system which includes Card readers with electric door strikes and contacts as well as Video surveillance cameras in common areas. | 2012 | 15 | 2027 | 2032 | 2025-03-28 | 2 - Good | No significant deficiencies were observed. | 4 | Each | 102897.59 | 1.3 | 1.15 | 1 | 615327.59 | 1 | Active | 1675 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 574 | Server room A/C | D303023 | Refrigerant DX Condensing Units - Over 20 Tons | The IT server room is provided with two LIEBERT, 40 ton, DX, A/C units. | 2003 | 18 | 2021 | 2026 | 2024-11-21 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 54878.71 | 1.3 | 1.15 | 1 | 656349.37 | 1 | Active | 1740 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 205 | Single door | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 2003 | 40 | 2043 | 2024 | 2024-01-02 | 5 - Very Poor | The interior doors have aged and some doors do not close properly. Lifecycle replacement is recommended. | 107 | Each | 2200 | 1.3 | 1.15 | 1 | 351923 | 1 | Active | 1713 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 133 | Single-Ply Membrane Roof Cover - Ballasted | B301023 | Conventional - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2012 | 20 | 2032 | 2032 | 2025-03-30 | 2 - Good | The roof is in good condition overall, no deficiencies were observed or reported. | 15622 | SM | 226.58 | 1.3 | 1.15 | 1 | 5291750.98 | 1 | Active | 1707 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 10 | Slab-on-Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab below grade. The basement floor acts as the slab on grade. | 2012 | 75 | 2087 | 2087 | 2023-11-15 | 1 - Very Good | Where exposed the slab on grade is in good condition overall, no major deficiencies were observed. | 37620 | SM Footprint | 85.91 | 1.3 | 1.15 | 1 | 4831741.63 | 0 | Active | 1670 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 6 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 2003 | 75 | 2078 | 2057 | 2023-11-11 | 1 - Very Good | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 32055 | SM Footprint | 85.91 | 1.3 | 1.15 | 1 | 4116998.35 | 0 | Active | 1712 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 272 | Universal Washroom | C104022 | Universal / Gender Neutral Washroom Refurbishment | The washrooms are provided with standard accessories. The washroom fixtures include floor-mounted water closets and porcelain lavatory sinks. | 2012 | 25 | 2037 | 2037 | 2025-07-14 | 1 - Very Good | The universal washrooms are in good condition overall, no significant deficiencies were observed. | 12 | Per Washroom | 15803.48 | 1.3 | 1.15 | 1 | 283514.43 | 1 | Active | 1734 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 728 | Variable Frequency Drives | D501025 | Main Service Disconnects | The electrical system is provided with variable frequency drives (VFDs) for the control of motor speeds. | 2012 | 40 | 2052 | 2032 | 2025-04-02 | 2 - Good | No significant deficiencies were observed. | 30 | Each | 13719.68 | 1.3 | 1.15 | 1 | 615327.65 | 1 | Active | 1736 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 480 | Water Heater - 50 Gal | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 189 L (50 gal), Rheem, electric, water heater rated at 9000 W. | 2003 | 20 | 2023 | 2025 | 2024-03-01 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 8232.48 | 1.3 | 1.15 | 1 | 24615.12 | 1 | Active | 1719 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 489 | Water Heater - Elec - Residential - 40 Gallon | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 151 Liter (40-gallon), electric, water heater rated at 3000 W | 2010 | 20 | 2030 | 2026 | 2024-11-03 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 8232.48 | 1.3 | 1.15 | 1 | 24615.12 | 1 | Active | 1678 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 490 | Water Tank Heater - 2005 | D202021 | Domestic Water Conditioners - Water Softener Systems | The water distribution system is provided with a RHEEM, 175 Liter (46 gal), electric, water tank heater. | 2005 | 20 | 2025 | 2026 | 2024-11-19 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 8232.48 | 1.3 | 1.15 | 1 | 24615.12 | 1 | Active | 1738 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 491 | Water Tank Heater - 2011 | D202021 | Domestic Water Conditioners - Water Softener Systems | The water distribution system is provided with a JOHN WOOD, 184 Liter (48 gal), electric, water tank heater. | 2011 | 20 | 2031 | 2026 | 2024-11-20 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred | 2 | Each | 8232.48 | 1.3 | 1.15 | 1 | 24615.12 | 1 | Active | 1739 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 670 | Wet Sprinkler System | D401002 | Sprinklers (Wet) | The fire protection system for the 1997 section of Block D consists of a wet sprinkler system that includes backflow prevention, distribution piping, spare sprinkler heads, fire department hose connections and shutoff valves. | 2003 | 40 | 2043 | 2032 | 2025-03-29 | 2 - Good | No significant deficiencies were observed. | 63701 | SM Building | 66.09 | 1.3 | 1.15 | 1 | 6293948.64 | 1 | Active | 1694 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 683 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection, distribution piping and shutoff valves | 2007 | 40 | 2047 | 2042 | 2025-09-15 | 1 - Very Good | No significant deficiencies observed. | 89297 | SM Building | 32.1 | 1.3 | 1.15 | 1 | 4285318.38 | 1 | Active | 1733 | Administrative | West Campus | North
| 22.054 | 9 | The Mustafar Visitor Center | Winnipeg | 82 | Window walls | B202001 | Windows | The exterior envelope of the building includes areas of window wall system with insulating glass. The window walls include operable units. | 2007 | 35 | 2042 | 2057 | 2023-12-02 | 1 - Very Good | No significant deficiencies were observed. | 2691 | SM | 1387.83 | 1.3 | 1.15 | 1 | 5583302.54 | 0 | Active | 1723 | Administrative | West Campus | North
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 401 | Acoustic Panel Ceiling - Perforated Metal Panel | C303008 | Metal Ceiling | The building's ceiling finishes include suspended perforated metal panel ceiling with concealed suspension system. | 2007 | 40 | 2047 | 2037 | 2025-07-22 | 1 - Very Good | The suspended ceiling tiles are in good condition overall, no major deficiencies were observed. | 36597 | SM | 151.06 | 1.3 | 1.15 | 1 | 8264872.52 | 1 | Active | 1803 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 373 | Acoustic Tile Ceiling - Exposed T-bar - 1997 | C303004 | Adhered Acoustic Tile Ceiling | The building's ceiling finishes include acoustic ceiling tiles with T-bar suspension system. | 1997 | 30 | 2027 | 2026 | 2024-11-28 | 4 - Poor | The ceiling tiles are in good condition overall, lifecycle replacement can be deferred. | 79653 | SM | 89.69 | 1.3 | 1.15 | 1 | 10680395.97 | 1 | Active | 1781 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 375 | Acoustical Ceiling Tiles | C303004 | Adhered Acoustic Tile Ceiling | The building’s ceiling finishes include suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids. | 2012 | 30 | 2042 | 2037 | 2025-07-16 | 1 - Very Good | The ceiling finish ACT tiles are in good condition overall, no deficiencies were observed. | 75993 | SM | 89.69 | 1.3 | 1.15 | 1 | 10189639.19 | 1 | Active | 1745 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 757 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring Systems | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1991 | 50 | 2041 | 2026 | 2024-11-26 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SM Building | 114.24 | 1.3 | 1.15 | 1 | 7893858.34 | 1 | Active | 1773 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 759 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring Systems | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1991 | 50 | 2041 | 2026 | 2024-12-04 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SM Building | 114.24 | 1.3 | 1.15 | 1 | 6482118.12 | 1 | Active | 1791 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 758 | Branch Wiring - Equipment & Devices - Average Density - 1972 | D502001 | Branch Wiring Systems | Branch wiring for the 1972 section of the building includes interior and exterior branch wiring, devices and utilization equipment. | 1991 | 50 | 2041 | 2026 | 2024-12-01 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 40828 | SM Building | 114.24 | 1.3 | 1.15 | 1 | 6972965.13 | 1 | Active | 1784 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 234 | Cabinets - Millwork | C103009 | Fixed Casework | Millwork includes wall and under counter cabinets and plastic laminate countertops without appliances located in the offices and Labs. | 2012 | 35 | 2047 | 2042 | 2025-09-19 | 1 - Very Good | The millwork is in good condition overall, no major deficiencies were observed. | 919 | LM | 1738.59 | 1.3 | 1.15 | 1 | 2388657.49 | 1 | Active | 1812 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 630 | Central AHU - Air Handler - 8000 CFM- AHU-1, AHU-4 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system includes two ENG AIR, Air Handling Units (AHU-1 & AHU-4) with chilled water coils and hot water coils. AHU-1, 7300 cfm AHU-4, 7960 cfm | 2007 | 40 | 2047 | 2047 | 2025-12-19 | 1 - Very Good | No significant deficiencies were observed. | 2 | Each | 358382.29 | 1.3 | 1.15 | 1 | 1071563.05 | 1 | Active | 1806 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 631 | Central AHU - Air Handler - 9600 CFM- AHU-3, AHU-5 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system includes two ENG AIR, Air Handling Units (AHU-3 & AHU-5) with chilled water coils and hot water coils, each having a capacity of 9600 CFM. | 2007 | 40 | 2047 | 2047 | 2025-12-20 | 1 - Very Good | No significant deficiencies were observed. | 2 | Each | 358382.29 | 1.3 | 1.15 | 1 | 1071563.05 | 1 | Active | 1807 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 309 | Ceramic Tile Wall Surface | C301023 | Ceramic Wall Tile | The interior wall finishes include ceramic tile wall finish located at the main entrance. | 2007 | 40 | 2047 | 2037 | 2025-07-21 | 1 - Very Good | The ceramic wall finish is in good condition overall. | 37674 | SM | 188.82 | 1.3 | 1.15 | 1 | 10634839 | 1 | Active | 1801 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 597 | Chilled Water - Building Chilled Water Distribution System | D304006 | Chilled Water Distribution Systems | The chilled water piping system includes distribution piping, valves and insulation, installed in the mechanical rooms for chilled water to the air handlers. | 1991 | 45 | 2036 | 2030 | 2025-03-05 | 3 - Fair | No significant deficiencies were observed. | 68781 | SM Building | 72.7 | 1.3 | 1.15 | 1 | 7475566.16 | 1 | Active | 1796 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 600 | Chilled Water Distribution System | D304006 | Chilled Water Distribution Systems | The HVAC system is provided with a chilled water distribution system which includes distribution piping, valves and insulation that provides chilled water to the air handlers. | 2007 | 45 | 2052 | 2052 | 2026-04-04 | 1 - Very Good | No significant deficiencies were observed. | 89297 | SM Building | 72.7 | 1.3 | 1.15 | 1 | 9705378.39 | 1 | Active | 1808 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 558 | Chiller CH-01 | D303003 | Water Cooled Chillers | Chilled water is provided from a 297.7 ton, McQuay, Model #: WSC063-DAABM, chiller, CRN-CH-01, with R134A, refrigerant, coupled with two evaporative fluid coolers located on the rooftop. It was reported that CH-01 provides chilled water for process cooling load in the labs. | 2012 | 30 | 2042 | 2037 | 2025-07-18 | 1 - Very Good | No significant deficiencies were observed. | 300 | Ton | 1377.45 | 1.3 | 1.15 | 1 | 617786.33 | 1 | Active | 1751 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 264 | Communal Washroom | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and counter top lavatory sinks. | 2005 | 25 | 2030 | 2030 | 2025-03-03 | 3 - Fair | The washrooms are in fair condition overall, no significant deficiencies were observed. | 14 | Per Lavatory | 21334.7 | 1.3 | 1.15 | 1 | 446535.27 | 1 | Active | 1789 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 267 | Communal Washroom | C104021 | Communal Washroom Refurbishment | The washrooms are provided with painted metal floor-mounted partitions, as well as standard accessories. The washroom fixtures include floor-mounted water closets, wall-mounted urinals, and porcelain lavatories. | 2012 | 25 | 2037 | 2037 | 2025-07-24 | 1 - Very Good | The washrooms are in good condition overall, no significant deficiencies were observed. | 20 | Per Lavatory | 21334.7 | 1.3 | 1.15 | 1 | 637907.53 | 1 | Active | 1811 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 57 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior envelope of the stairwells is 8" split-rib concrete masonry unit construction. | 1991 | 75 | 2066 | 2047 | 2025-12-11 | 1 - Very Good | The split face concrete masonry unit is in fair condition overall, no significant deficiencies were observed or reported. | 8396 | SM | 726.96 | 1.3 | 1.15 | 1 | 9124816.46 | 1 | Active | 1766 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 58 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior wall includes split face concrete masonry unit with CMU backup | 1991 | 75 | 2066 | 2047 | 2025-12-15 | 1 - Very Good | The exterior wall is in fair condition overall, no significant deficiencies were observed. | 6674 | SM | 726.96 | 1.3 | 1.15 | 1 | 7253337.9 | 1 | Active | 1776 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 157 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) painted hollow concrete masonry walls. | 1991 | 75 | 2066 | 2057 | 2023-12-17 | 1 - Very Good | The interior partitions are in good condition overall, no deficiencies were observed. | 68781 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 20386598.98 | 0 | Active | 1794 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 172 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) concrete masonry walls. | 1991 | 75 | 2066 | 2047 | 2025-12-12 | 1 - Very Good | The interior walls are in good condition overall, no significant deficiencies were observed or reported. | 46220 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 13699547.91 | 1 | Active | 1768 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 174 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) concrete masonry walls. | 1991 | 75 | 2066 | 2047 | 2025-12-16 | 1 - Very Good | The interior walls are in good condition overall, no significant deficiencies were observed or reported. | 63701 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 18880893.59 | 1 | Active | 1778 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 554 | Condensing Boilers | D302015 | Hot Water Boilers - Over 1000 MBH | Heating hot water is provided from two 2,500MBH, CLEAVER BROOKS, Model: CFC-700-2500-125-HW, condensing boilers. | 2012 | 30 | 2042 | 2042 | 2025-09-16 | 1 - Very Good | No significant deficiencies were observed. | 5000 | MBH | 73.37 | 1.3 | 1.15 | 1 | 548440.75 | 1 | Active | 1750 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 573 | Cooling Towers | D303021 | Refrigerant DX Condensing Units - Under 5 Tons | The HVAC equipment is provided with four 300 ton, roof-mounted, galvanized, cooling towers. | 2012 | 18 | 2030 | 2037 | 2025-07-19 | 1 - Very Good | No significant deficiencies were observed. | 80 | Each | 5488.32 | 1.3 | 1.15 | 1 | 656403.07 | 1 | Active | 1752 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 669 | DDC System | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system compatible with Johnson Metasys for system optimization, pc control, with moderate sensor types and quantities. | 2012 | 20 | 2032 | 2032 | 2025-04-04 | 2 - Good | No significant deficiencies were observed. | 175861 | SM Building | 36.82 | 1.3 | 1.15 | 1 | 9680427.02 | 1 | Active | 1753 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 718 | Distribution Paneboards | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system for this building includes distribution panelboards, feeders and associated equipment. | 2012 | 40 | 2052 | 2052 | 2026-04-11 | 1 - Very Good | No significant deficiencies were observed. | 5 | Each | 142685.11 | 1.3 | 1.15 | 1 | 1066571.2 | 1 | Active | 1813 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 719 | Distribution Switchboards | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system is provided with distribution switchboards. | 2012 | 40 | 2052 | 2052 | 2026-04-12 | 1 - Very Good | No significant deficiencies were observed. | 5 | Each | 142685.11 | 1.3 | 1.15 | 1 | 1066571.2 | 1 | Active | 1817 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 469 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4” for main branch pipe, distribution piping, backflow preventer, water meter, valves, insulation and fittings. | 2007 | 40 | 2047 | 2047 | 2025-12-18 | 1 - Very Good | No significant deficiencies were observed. | 89297 | SM Building | 48.15 | 1.3 | 1.15 | 1 | 6427977.57 | 1 | Active | 1804 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 576 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1991 | 50 | 2041 | 2026 | 2024-11-23 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SM Building | 144.45 | 1.3 | 1.15 | 1 | 7726573.44 | 1 | Active | 1764 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 578 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1991 | 50 | 2041 | 2026 | 2024-12-02 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SM Building | 144.45 | 1.3 | 1.15 | 1 | 6015795.76 | 1 | Active | 1788 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 579 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1991 | 50 | 2041 | 2026 | 2024-12-03 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SM Building | 144.45 | 1.3 | 1.15 | 1 | 8196270.67 | 1 | Active | 1790 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 577 | Ductwork Distribution System - 1972 | D304001 | Air Distribution Systems | The HVAC system for the 1972 section of the building includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1991 | 50 | 2041 | 2026 | 2024-11-30 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 40828 | SM Building | 144.45 | 1.3 | 1.15 | 1 | 8816918.88 | 1 | Active | 1783 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 405 | Elevators - 5 Levels | D101003 | Freight Elevators - Up to 3 Floors (Hydraulic) | The building contains two KONE traction elevators, #1 & #3, both rated 2,206 Kg (5000LBS) which serve 5 floors of the building; and one elevator, #2, which serves the 100 and 200 levels of the building. The elevator cab finishes consist of stainless steel doors, door returns, and walls with textured rubber flooring. | 2012 | 30 | 2042 | 2037 | 2025-07-17 | 1 - Very Good | No significant deficiencies were observed. | 3 | Each | 196393.23 | 1.3 | 1.15 | 1 | 880823.64 | 1 | Active | 1746 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 906 | Exterior windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 2024 | 35 | 2059 | 2058 |  | 1 - Very Good |  | 5274 | SM | 1387.83 | 1.3 | 1.15 | 1 | 10942526.05 | 0 | Active |  | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 802 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes pull stations at all exit doors, audio devices, visual devices and smoke detectors. | 1998 | 20 | 2018 | 2025 | 2024-03-05 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 89986 | SM Building | 60.42 | 1.3 | 1.15 | 1 | 8128246.41 | 1 | Active | 1759 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 829 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system that includes a maim fire alarm control panel and a number of secondary control panels throughout the building. | 2014 | 20 | 2034 | 2034 | 2025-05-14 | 2 - Good | No significant deficiencies were observed. | 89986 | SM Building | 60.42 | 1.3 | 1.15 | 1 | 8128246.41 | 1 | Active | 1760 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 803 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building includes a fire alarm system that includes all conduit, wire, and connections to the main control panel, pull stations audio/visual strobes, smoke detectors and control panels. | 1998 | 20 | 2018 | 2025 | 2024-03-06 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 89986 | SM Building | 60.42 | 1.3 | 1.15 | 1 | 8128246.41 | 1 | Active | 1761 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 501 | Gas-Fired Water Heater | D202031 | Domestic Water Heat Exchangers | Domestic hot water is provided from three 1,000MBH, semi-instantaneous, gas fired, water heaters, each with 1116gph recovery that includes recirculation pump and 552gal storage tank. | 2012 | 30 | 2042 | 2027 | 2025-01-11 | 4 - Poor | No significant deficiencies were observed. | 50 | Each | 10976.65 | 1.3 | 1.15 | 1 | 820504.59 | 1 | Active | 1747 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 173 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1991 | 75 | 2066 | 2047 | 2025-12-13 | 1 - Very Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 46220 | SM Building | 198.26 | 1.3 | 1.15 | 1 | 13699547.91 | 1 | Active | 1769 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 590 | Heating Hot Water - Building Hot Water Distribution System | D304003 | Heating Water Distribution Systems | The building heating hot water distribution system includes distribution piping, valves and insulation. | 1991 | 45 | 2036 | 2030 | 2025-03-06 | 3 - Fair | No significant deficiencies were observed. | 68781 | SM Building | 108.57 | 1.3 | 1.15 | 1 | 11163991.99 | 1 | Active | 1797 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 589 | HHW Piping | D304003 | Heating Water Distribution Systems | The HVAC system is provided with heating hot water (HHW) piping, valves and pumps. | 1991 | 45 | 2036 | 2026 | 2024-12-05 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 63701 | SM Building | 108.57 | 1.3 | 1.15 | 1 | 10339446.27 | 1 | Active | 1818 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 700 | High Voltage Electrical Service | D501021 | Low Voltage Electrical Service | The building is provided with a 13.8kV, 600A main electrical service switchgear. | 2012 | 40 | 2052 | 2052 | 2026-04-09 | 1 - Very Good | No significant deficiencies were observed. | 175990 | SM Building | 36.82 | 1.3 | 1.15 | 1 | 9687527.94 | 1 | Active | 1814 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 217 | Interior Hollow Metal Swing Doors - Single Leaf - Nonrated | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 1991 | 40 | 2031 | 2026 | 2024-11-25 | 4 - Poor | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 135 | Each | 2200 | 1.3 | 1.15 | 1 | 444015 | 1 | Active | 1771 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 184 | Interior Windows - Metal | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 400 and 300 floors. | 1991 | 75 | 2066 | 2026 | 2024-11-24 | 4 - Poor | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 10010 | SM | 793.05 | 1.3 | 1.15 | 1 | 11867953.6 | 1 | Active | 1770 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 131 | Inverted Roof Membrane Assembly | B301023 | Conventional - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2010 | 20 | 2030 | 2030 | 2025-03-04 | 3 - Fair | The roof is good condition overall, no deficiencies were observed. | 30105 | SM | 226.58 | 1.3 | 1.15 | 1 | 10197680.4 | 1 | Active | 1793 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 532 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes a acid water waste glass piping system for the laboratories. | 1991 | 30 | 2021 | 2026 | 2024-11-29 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 50773 | SM | 96.3 | 1.3 | 1.15 | 1 | 7309712.65 | 1 | Active | 1782 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 768 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts, conduit and wire. | 2000 | 35 | 2035 | 2030 | 2025-02-28 | 3 - Fair | No significant deficiencies were observed. | 46220 | SM Building | 101.96 | 1.3 | 1.15 | 1 | 7045323.84 | 1 | Active | 1774 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 769 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of recessed and surface mounted fluorescent fixtures with T-8 lamps and electronic ballasts including conduit and wire . | 2000 | 35 | 2035 | 2030 | 2025-03-01 | 3 - Fair | No significant deficiencies were observed. | 63701 | SM Building | 101.96 | 1.3 | 1.15 | 1 | 9709956.17 | 1 | Active | 1785 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 771 | Lighting Fixtures - Interior | D502002 | Interior Lighting Systems | The interior lighting system consists of recessed and surface mounted fluorescent fixtures with T- 8 lamps, conduit and wire. About 25% of the lamps are equipped with emergency power. | 2005 | 35 | 2040 | 2035 | 2025-06-04 | 2 - Good | No significant deficiencies were observed. | 68781 | SM Building | 101.96 | 1.3 | 1.15 | 1 | 10484301.59 | 1 | Active | 1799 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 867 | Lightning Protection System | D509004 | Lightning Protection Systems | The electrical system is provided with a lightning protection system. | 2012 | 50 | 2062 | 2062 | 2026-04-16 | 1 - Very Good | No significant deficiencies were observed. | 175990 | SM Building | 30.21 | 1.3 | 1.15 | 1 | 7948403.56 | 0 | Active | 1816 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 717 | Main Distribution Switchboard | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system is provided with a 3,000A, 600Y/347V, 3-Phase, 4-Wire, double ended, SQUARE D, main breaker, distribution switchboard with tie breaker. | 2012 | 40 | 2052 | 2052 | 2026-04-10 | 1 - Very Good | No significant deficiencies were observed. | 5 | Each | 142685.11 | 1.3 | 1.15 | 1 | 1066571.2 | 1 | Active | 1755 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 739 | Main Electrical System Transformer | D501026 | Grounding Methods | The electrical system for the building is provided with a 2500 kVA, 13.8kV - 600Y/347V, main transformer. | 1991 | 50 | 2041 | 2026 | 2024-12-06 | 4 - Poor | No significant deficiencies were observed. Replacement can be deferred. | 35 | Each | 13719.68 | 1.3 | 1.15 | 1 | 717882.26 | 1 | Active | 1819 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 541 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 1998 | 40 | 2038 | 2038 | 2025-08-06 | 1 - Very Good | No significant deficiencies were observed. | 161459 | SM | 24.55 | 1.3 | 1.15 | 1 | 5925908.58 | 1 | Active | 1757 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 545 | Natural Gas Supply | D301002 | Natural Gas Supply Piping and Fittings | The building is provided with a natural gas piping system and supply from the local utility. | 2012 | 40 | 2052 | 2052 | 2026-03-28 | 1 - Very Good | No significant deficiencies were observed. | 175861 | SM | 24.55 | 1.3 | 1.15 | 1 | 6454494.39 | 1 | Active | 1749 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 295 | Paint | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, and concrete walls. | 2012 | 10 | 2022 | 2025 | 2024-03-03 | 5 - Very Poor | The painted wall finish is in good condition overall, lifecycle replacement can be deferred. | 168173 | SM Building | 50.04 | 1.3 | 1.15 | 1 | 12580988.5 | 1 | Active | 1744 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 777 | Pendant Fixtures | D502002 | Interior Lighting Systems | The dining areas and the central 200-300 level open corridors are provided with decorative pendant mounted fixtures which are tied into a Lutron lighting control system that consists of lighting schedules, as well as passive infrared and ultrasonic occupancy sensors. Selected fixtures contain emergency battery backup ballasts to provide egress lighting in the event of an outage. | 2012 | 35 | 2047 | 2042 | 2025-09-17 | 1 - Very Good | No significant deficiencies were observed. | 58663 | SM Building | 101.96 | 1.3 | 1.15 | 1 | 8942012.82 | 1 | Active | 1756 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 646 | Perimeter Heat System - Hydronic Fin Tube | D305004 | Finned Tube Radiation Units | The HVAC equipment includes a two-pipe system of heating hot water with hydronic fin tube perimeter units. | 2007 | 30 | 2037 | 2037 | 2025-07-23 | 1 - Very Good | No significant deficiencies were observed. | 6000 | SM | 60.96 | 1.3 | 1.15 | 1 | 546811.2 | 1 | Active | 1809 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 155 | Phytotron Skylight | B302021 | Skylights | Aluminum-framed phytotron skylight with vertical insulated glazing units and slope single-glazing units. | 2012 | 25 | 2037 | 2037 | 2025-07-15 | 1 - Very Good | The phytotron skylight is continuously leaking due to a design deficiency. Repairs to the system are currently ongoing between the University and building (in litigation). | 3445 | SM | 1661.62 | 1.3 | 1.15 | 1 | 8557799.95 | 1 | Active | 1743 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 64 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels. | 1991 | 75 | 2066 | 2047 | 2025-12-09 | 1 - Very Good | The exterior wall system is in a fair condition overall, no significant deficiencies were observed. | 5167 | SM | 830.81 | 1.3 | 1.15 | 1 | 6417728.93 | 1 | Active | 1763 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 65 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels with concrete masonry unit back-up. | 1991 | 75 | 2066 | 2047 | 2025-12-17 | 1 - Very Good | No significant deficiencies were observed or reported. | 7427 | SM | 830.81 | 1.3 | 1.15 | 1 | 9224786.68 | 1 | Active | 1787 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 833 | Public Address System | D503004 | Public Address and Music Systems | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 1998 | 15 | 2013 | 2025 | 2024-03-04 | 5 - Very Poor | No significant deficiencies were observed. Replacement can be deferred. | 269980 | SM Building | 24.55 | 1.3 | 1.15 | 1 | 9908873.46 | 1 | Active | 1758 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 530 | Rainwater Drainage | D204001 | Rain Water Drainage Piping and Fittings | The building is provided with a rain water drainage includes interior piping, roof drains and pumped discharge to the municipal main. | 2012 | 50 | 2062 | 2062 | 2026-03-27 | 1 - Very Good | No significant deficiencies were observed. | 175861 | SM Building | 34.93 | 1.3 | 1.15 | 1 | 9183522.97 | 0 | Active | 1748 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 24 | Roof Deck - Concrete on Permanent Steel Form On Steel Frame | B103006 | Structural Steel Frame | The 5th floor mechanical penthouse roof deck is a concrete infilled metal pan deck on open web steel joists. No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 2007 | 75 | 2082 | 2082 | 2023-11-21 | 1 - Very Good | No significant deficiencies were observed or reported. | 5570 | SM Building | 494.71 | 1.3 | 1.15 | 1 | 4119524.38 | 0 | Active | 1800 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 25 | Roof Deck - Metal Deck on Steel Frame | B103006 | Structural Steel Frame | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1991 | 75 | 2066 | 2030 | 2025-03-02 | 3 - Fair | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 3426 | SM Building | 494.71 | 1.3 | 1.15 | 1.2 | 3040608.37 | 1 | Active | 1786 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 28 | Roof Deck - Metal Deck on Steel Frame | B103006 | Structural Steel Frame | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1991 | 75 | 2066 | 2047 | 2025-12-10 | 1 - Very Good | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 4330 | SM Building | 494.71 | 1.3 | 1.15 | 1 | 3202430.98 | 1 | Active | 1765 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 29 | Roof Deck - Metal Deck on Steel Frame | B103006 | Structural Steel Frame | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1991 | 75 | 2066 | 2047 | 2025-12-14 | 1 - Very Good | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 5489 | SM Building | 494.71 | 1.3 | 1.15 | 1 | 4059617.47 | 1 | Active | 1775 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 515 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron piping, copper and PVC with gravity discharge to the municipal system. | 2007 | 50 | 2057 | 2057 | 2026-03-24 | 1 - Very Good | No significant deficiencies were observed. | 89297 | SM Building | 54.76 | 1.3 | 1.15 | 1 | 7310406.06 | 0 | Active | 1805 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 855 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility utilizes a card access security system to monitor strategic doors within the facility which consists of controllers, swipe and proximity card readers, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2025-02-27 | 3 - Fair | No significant deficiencies were observed. | 6 | Each | 102897.59 | 1.3 | 1.15 | 1 | 922991.38 | 1 | Active | 1762 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 339 | Sheet Vinyl Goods Flooring | C302006 | Masonry and Stone Floor | Floor finishes located in the classrooms on the 400 and 300 floor levels include areas of sheet vinyl flooring and related base. | 2007 | 50 | 2057 | 2025 | 2024-03-07 | 5 - Very Poor | The sheet vinyl floor finish is in good condition overall, lifecycle replacement can be deferred. | 9053 | SM | 849.69 | 1.3 | 1.15 | 1 | 11499904.14 | 1 | Active | 1802 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 218 | Single door | C102008 | Interior Doors - Hollow Metal or Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on metal frames. | 1991 | 40 | 2031 | 2026 | 2024-11-27 | 4 - Poor | No significant deficiencies were observed or reported at the time of the field review. Lifecycle replacement can be deferred. | 165 | Each | 2200 | 1.3 | 1.15 | 1 | 542685 | 1 | Active | 1779 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 50 | Split Face Concrete Masonry Unit | B201021 | Masonry | The building's exterior wall include sections of concrete masonry unit. | 1991 | 75 | 2066 | 2057 | 2023-11-23 | 1 - Very Good | The exterior wall is in fair condition overall, no significant deficiencies were observed or reported. | 6523 | SM | 726.96 | 1.3 | 1.15 | 1 | 7089230.32 | 0 | Active | 1792 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 684 | Standpipes | D402001 | Standpipes | The building is equipped with a standpipe system with approximately 6 fire hose cabinets located on each floor. The standpipe system is supplied by a 25HP, 500GPM fire pump located in Mechanical room 162. | 2012 | 40 | 2052 | 2047 | 2025-12-08 | 1 - Very Good | No significant deficiencies were observed. | 175990 | SM Building | 32.1 | 1.3 | 1.15 | 1 | 8445672.11 | 1 | Active | 1754 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 587 | Steam Distribution System | D304002 | Steam Distribution Systems | The HVAC system includes a steam distribution piping and pump system including condensate return tank with pumps. | 2012 | 45 | 2057 | 2057 | 2026-03-31 | 1 - Very Good | No significant deficiencies were observed. | 175990 | SM Building | 132.17 | 1.3 | 1.15 | 0.3 | 10432378.34 | 0 | Active | 1815 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 752 | Transformer - 1250 KVA | D501026 | Grounding Methods | The main electrical service isprovided with 1250 KVA, 15 kV - 600Y/347V transformers located in the Main Electrical Vault. | 1991 | 50 | 2041 | 2048 | 2026-01-18 | 1 - Very Good | No significant deficiencies were observed. | 45 | Each | 13719.68 | 1.3 | 1.15 | 1 | 922991.47 | 1 | Active | 1798 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 358 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Sheet Floor | The building's floor finishes include asbestos containing vinyl floor tiles located in the laboratories and the corridors. | 1991 | 15 | 2006 | 2024 | 2024-01-07 | 5 - Very Poor | The vinyl tiles have aged significantly and are in very poor condition overall, life cycle replacement is recommended. Note that cost includes abatement of asbestos. | 29315 | SM | 119.6 | 1.3 | 1.15 | 2 | 10483161.26 | 1 | Active | 1795 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 907 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Sheet Floor | The building's floor finish includes asbestos containing vinyl tiles. | 2025 | 15 | 2040 | 2039 |  | 1 - Very Good |  | 43926 | SM | 119.6 | 1.3 | 1.15 | 1.5 | 11781084.98 | 0 | Active |  | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 357 | Vinyl Tile Flooring - 1972 | C302022 | Vinyl Tile / Sheet Floor | The building's floor finish includes asbestos containing vinyl tiles located in the corridors and labs. | 1991 | 15 | 2006 | 2024 | 2024-01-06 | 5 - Very Poor | The vinyl tiles are in poor condition overall, lifecycle replacement is recommended. Note that costing includes asbestos abatement. | 24757 | SM | 119.6 | 1.3 | 1.15 | 2 | 8853202.23 | 1 | Active | 1780 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 672 | Wet Sprinkler System - Piping | D401002 | Sprinklers (Wet) | The fire protection systems include a wet sprinkler system with backflow preventer, distribution piping, shutoff valves, fire department hose connections and spare sprinkler heads. | 2007 | 40 | 2047 | 2042 | 2025-09-18 | 1 - Very Good | No significant deficiencies were observed. | 89297 | SM Building | 66.09 | 1.3 | 1.15 | 1 | 8822949.9 | 1 | Active | 1810 | Administrative | Main Campus | West
| 12.01 | 10 | University Teaching and Outreach Ctr | Vancouver | 90 | Window Wall - 2005 | B202001 | Windows | The buildings fenestration includes custom aluminum framed sash with insulating glass. | 2005 | 35 | 2040 | 2037 | 2025-07-20 | 1 - Very Good | The windows are in good condition overall, no significant deficiencies. | 3660 | SM | 1387.83 | 1.3 | 1.15 | 1 | 7593789.41 | 1 | Active | 1777 | Administrative | Main Campus | West