## Overview
SLAMUSA_Element Recommendations_rec_year_all
Generated on | March 24, 2026
Generated for | SLAM USA
Generated by | Bill Roth
Asset | - All -
Uniformat Code | - All -
Recommendation Type | - All -
Statuses | Active

## Data
Flags | Rec ID | Facility # | Asset ID | Asset Name | City | Element ID | Element Descriptor | Element Description | Year Installed | Last Assessment | Condition | Condition Narrative | Expected Useful Life | Expected Renewal Year | Observed Renewal Year | Remaining Useful Life | Element Qty | Element Units | Element Unit Cost | Replacement Factor | Soft Cost Factor | Regional Factor | Difficulty Factor | Element Cost | Uniformat Code | Uniformat Name | Rec Name | Rec Type | Status | Rec Description | Priority | MVP Score | Rec Year | Rec Qty | Rec Units | Rec Unit Cost | Rec Cost | Task Count | Task Coverage | Task Estimated Cost | Task Actual Cost | Asset Type | Zone
| 20 | 04.758 | 1 | Humanities Fine Arts | Morris | 18 | Air Handling Unit - Wine Cellar | The HVAC system includes an air handling unit with a cooling capacity of 5 tons for the wine cellar with chilled water cooling coils. | 1998 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 45 | 2043 | 2026 | 1 | 14500 | SF | 4.36 | 1.25 | 1.3 | 1.25 | 1 | 102732.5 | D304011 | Refrigerant Distribution Systems | Refrigerant Distribution Systems | Life Cycle Replacement | Active | Replace Refrigerant Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 14500 | SF | 4.36 | 128415.63 | 0 | 6.9% | 10000 | 0 | Academic | Central
| 93 | 04.758 | 1 | Humanities Fine Arts | Morris | 93 | Boiler HW - 1982 | Heating Hot Water is provided from a Chromalox electric steam boiler rated at 82 MBH (24 KW). | 1982 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2012 | 2026 | 1 | 82 | MBH | 70.84 | 1.25 | 1.3 | 1.25 | 1 | 9439.43 | D302002 | Hot Water Boilers - Up to 1000 MBH | Hot Water Boilers - Up to 1000 MBH | Life Cycle Replacement | Active | Replace Hot Water Boilers - Up to 1000 MBH | Priority 4: Proactive Replacement | 66 | 2026 | 82 | MBH | 70.84 | 11799.29 | 0 | 1219.51% | 10000 | 0 | Academic | Central
| 94 | 04.758 | 1 | Humanities Fine Arts | Morris | 94 | Boiler HW - 1990 | Heating medium is provided from a Caloritech electric steam boiler rated at approximately 40 MBH (12 kW). | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2020 | 2026 | 1 | 41 | MBH | 70.84 | 1.25 | 1.3 | 1.25 | 1 | 4719.72 | D302002 | Hot Water Boilers - Up to 1000 MBH | Hot Water Boilers - Up to 1000 MBH | Life Cycle Replacement | Active | Replace Hot Water Boilers - Up to 1000 MBH | Priority 4: Proactive Replacement | 66 | 2026 | 41 | MBH | 70.84 | 5899.64 | 0 | 2439.02% | 10000 | 0 | Academic | Central
| 65 | 04.758 | 1 | Humanities Fine Arts | Morris | 64 | Custodial Sinks | The plumbing fixtures include custodial sinks installed on two floors. | 2000 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2030 | 2026 | 1 | 2 | Each | 1955.8 | 1.25 | 1.3 | 1.25 | 1 | 6356.35 | D201016 | Custodial Sinks | Custodial Sinks | Life Cycle Replacement | Active | Replace Custodial Sinks | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 1955.8 | 7945.44 | 0 | 50000% | 10000 | 0 | Academic | Central
| 115 | 04.758 | 1 | Humanities Fine Arts | Morris | 117 | Custodial Sinks | The plumbing fixtures include flooor-mounted custodial sinks. | 1972 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2002 | 2026 | 1 | 3 | Each | 1955.8 | 1.25 | 1.3 | 1.25 | 1 | 9534.53 | D201016 | Custodial Sinks | Custodial Sinks | Life Cycle Replacement | Active | Replace Custodial Sinks | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 1955.8 | 11918.16 | 0 | 33333.33% | 10000 | 0 | Academic | Central
| 83 | 04.758 | 1 | Humanities Fine Arts | Morris | 82 | Custodial Sinks - 1972 | The plumbing fixtures include custodial sinks. | 1972 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2002 | 2026 | 1 | 2 | Each | 1955.8 | 1.25 | 1.3 | 1.25 | 1 | 6356.35 | D201016 | Custodial Sinks | Custodial Sinks | Life Cycle Replacement | Active | Replace Custodial Sinks | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 1955.8 | 7945.44 | 0 | 50000% | 10000 | 0 | Academic | Central
| 80 | 04.758 | 1 | Humanities Fine Arts | Morris | 79 | Custodial Sinks - 2000 | The plumbing fixtures include a custodial sink installed on the 2nd floor. | 2000 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred | 30 | 2030 | 2026 | 1 | 1 | Each | 1955.8 | 1.25 | 1.3 | 1.25 | 1 | 3178.18 | D201016 | Custodial Sinks | Custodial Sinks | Life Cycle Replacement | Active | Replace Custodial Sinks | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 1955.8 | 3972.72 | 0 | 100000% | 10000 | 0 | Academic | Central
| 92 | 04.758 | 1 | Humanities Fine Arts | Morris | 92 | Custodial/Utility Sinks | The plumbing fixtures include custodial/utility sink in the janitor's closet on each floor. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2020 | 2026 | 1 | 2 | Each | 1955.8 | 1.25 | 1.3 | 1.25 | 1 | 6356.35 | D201016 | Custodial Sinks | Custodial Sinks | Life Cycle Replacement | Active | Replace Custodial Sinks | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 1955.8 | 7945.44 | 0 | 50000% | 10000 | 0 | Academic | Central
| 84 | 04.758 | 1 | Humanities Fine Arts | Morris | 83 | Drinking Water Fountains | Plumbing fixtures include wall mounted stainless steel drinking water fountains in the corridors. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2020 | 2026 | 1 | 2 | Each | 1466.85 | 1.25 | 1.3 | 1.25 | 1 | 4767.26 | D201006 | Drinking Water Fountains (Non-refrigerated) | Drinking Water Fountains (Non-refrigerated) | Life Cycle Replacement | Active | Replace Drinking Water Fountains (Non-refrigerated) | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 1466.85 | 5959.08 | 0 | 50000% | 10000 | 0 | Academic | Central
| 69 | 04.758 | 1 | Humanities Fine Arts | Morris | 68 | DX Ductless Split Unit | Cooling for the Main Electrical Vault is provided by a 2 ton ductless split DX unit. | 2008 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2026 | 2026 | 1 | 2 | Each | 3743.74 | 1.25 | 1.3 | 1.25 | 1 | 12167.16 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 3743.74 | 15208.94 | 0 | 50000% | 10000 | 0 | Academic | Central
| 85 | 04.758 | 1 | Humanities Fine Arts | Morris | 84 | DX Ductless Split Unit | Cooling for the walk in cooler is provided by a 2 ton ductless split DX refrigerant unit. | 2008 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2026 | 2026 | 1 | 2 | Each | 3743.74 | 1.25 | 1.3 | 1.25 | 1 | 12167.16 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 3743.74 | 15208.94 | 0 | 50000% | 10000 | 0 | Academic | Central
| 70 | 04.758 | 1 | Humanities Fine Arts | Morris | 69 | Exhaust System - Fume Hood | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2015 | 2026 | 1 | 2 | Each | 4679.29 | 1.25 | 1.3 | 1.25 | 1 | 15207.69 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 4679.29 | 19009.62 | 0 | 50000% | 10000 | 0 | Academic | Central
| 29 | 04.758 | 1 | Humanities Fine Arts | Morris | 27 | Exhaust System - Fume Hood - Ductwork/Fan | The exhaust system for the labs includes constant volume fume hoods and exhaust systems. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2015 | 2026 | 1 | 2 | Each | 4679.29 | 1.25 | 1.3 | 1.25 | 1 | 15207.69 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 4679.29 | 19009.62 | 0 | 50000% | 10000 | 0 | Academic | Central
| 95 | 04.758 | 1 | Humanities Fine Arts | Morris | 95 | Exhaust System Fans | The HVAC system includes exhaust fans installed on the roof and throughout the building. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2015 | 2026 | 1 | 2 | Each | 2808.19 | 1.25 | 1.3 | 1.25 | 1 | 9126.62 | D304031 | Exhaust Fans - Centrifugal | Exhaust Fans - Centrifugal | Life Cycle Replacement | Active | Replace Exhaust Fans - Centrifugal | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 2808.19 | 11408.27 | 0 | 50000% | 10000 | 0 | Academic | Central
| 106 | 04.758 | 1 | Humanities Fine Arts | Morris | 107 | Exit Signs | The building is provided with exit signs showing to indicate the direction to the means of egress and includes single and double sided LED exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2010 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2045 | 2026 | 1 | 350 | SF | 20.89 | 1.25 | 1.3 | 1.25 | 1 | 11881.19 | D502022 | Interior Lighting (Industrial) | Interior Lighting (Industrial) | Life Cycle Replacement | Active | Replace Interior Lighting (Industrial) | Priority 4: Proactive Replacement | 0 | 2026 | 350 | SF | 20.89 | 14851.48 | 0 | 285.71% | 10000 | 0 | Academic | Central
| 51 | 04.758 | 1 | Humanities Fine Arts | Morris | 50 | Exterior Automatic Openers - Single | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2010 | 2019-10-15 | 2 - Good | The automatic door openers are in good condition and functioning as intended. Lifecycle replacement can be deferred. | 15 | 2025 | 2026 | 1 | 1 | Each | 3743.74 | 1.25 | 1.3 | 1.25 | 1 | 6083.58 | B203008 | Exterior - Automatic Door Openers | Exterior - Automatic Door Openers | Life Cycle Replacement | Active | Replace Exterior - Automatic Door Openers | Priority 4: Proactive Replacement | 34 | 2026 | 1 | Each | 3743.74 | 7604.47 | 0 | 100000% | 10000 | 0 | Academic | Central
| 24 | 04.758 | 1 | Humanities Fine Arts | Morris | 22 | Exterior Hollow Metal Door - Single Leaf | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 2019-10-15 | 2 - Good | The interior doors are in fair condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 2 | Each | 2995.3 | 1.25 | 1.3 | 1.25 | 1 | 9734.73 | B203023 | Exterior - Single Door - Hollow Metal | Exterior - Single Door - Hollow Metal | Life Cycle Replacement | Active | Replace Exterior - Single Door - Hollow Metal | Priority 4: Proactive Replacement | 34 | 2026 | 2 | Each | 2995.3 | 12168.41 | 2 | 50000% | 10000 | 0 | Academic | Central
| 75 | 04.758 | 1 | Humanities Fine Arts | Morris | 74 | Exterior Soffits | The building includes prefinished metal soffits located at the loading dock. | 1972 | 2019-10-15 | 2 - Good | The soffits are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 50 | 2022 | 2026 | 1 | 527 | SF | 9.59 | 1.25 | 1.3 | 1.25 | 1 | 8212.64 | B201008 | Exterior Soffits | Exterior Soffits | Life Cycle Replacement | Active | Replace Exterior Soffits | Priority 4: Proactive Replacement | 44 | 2026 | 527 | SF | 9.59 | 10265.8 | 0 | 189.75% | 10000 | 0 | Academic | Central
| 90 | 04.758 | 1 | Humanities Fine Arts | Morris | 89 | Exterior Stairs - Concrete | The building includes cast in place stairs located at the loading dock area. | 1972 | 2019-10-15 | 2 - Good | The concrete stairs are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 40 | 2012 | 2026 | 1 | 2 | Per Riser | 936.32 | 1.25 | 1.3 | 1.25 | 1 | 3043.04 | C201002 | Exterior (Attached) Stair Construction | Exterior (Attached) Stair Construction | Life Cycle Replacement | Active | Replace Exterior (Attached) Stair Construction | Priority 4: Proactive Replacement | 41 | 2026 | 2 | Per Riser | 936.32 | 3803.8 | 0 | 50000% | 10000 | 0 | Academic | Central
| 41 | 04.758 | 1 | Humanities Fine Arts | Morris | 39 | Exterior Storefront Door - Single Leaf | The exterior doors of hollow metal glazed single - door mounted by butt hinges to metal door frame. | 2005 | 2019-10-15 | 2 - Good | The exterior door is in good condition overall, lifecycle replacement can be deferred. | 25 | 2030 | 2026 | 1 | 1 | Lump Sum | 7700 | 1.25 | 1.3 | 1.25 | 1 | 12512.5 | B203005 | Exterior - Hangar Doors | Exterior - Hangar Doors | Life Cycle Replacement | Active | Replace Exterior - Hangar Doors | Priority 4: Proactive Replacement | 34 | 2026 | 1 | Lump Sum | 7700 | 15640.63 | 0 | 100000% | 10000 | 0 | Academic | Central
| 56 | 04.758 | 1 | Humanities Fine Arts | Morris | 55 | Gypsum Board Ceiling - Fire Resistant | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 2019-10-15 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 15 | 1987 | 2026 | 1 | 3122 | SF | 2.65 | 1.25 | 1.3 | 1.25 | 1 | 13444.11 | C303006 | Painted Ceiling Structures | Painted Ceiling Structures | Life Cycle Replacement | Active | Replace Painted Ceiling Structures | Priority 4: Proactive Replacement | 31 | 2026 | 3122 | SF | 2.65 | 16805.14 | 0 | 32.03% | 10000 | 0 | Academic | Central
| 79 | 04.758 | 1 | Humanities Fine Arts | Morris | 78 | Gypsum Board Ceiling - Fire Resistant | The building's ceiling finishes include GWB ceiling located in the corridors. | 1972 | 2019-10-15 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 15 | 1987 | 2026 | 1 | 2791 | SF | 2.65 | 1.25 | 1.3 | 1.25 | 1 | 12018.74 | C303006 | Painted Ceiling Structures | Painted Ceiling Structures | Life Cycle Replacement | Active | Replace Painted Ceiling Structures | Priority 4: Proactive Replacement | 31 | 2026 | 2791 | SF | 2.65 | 15023.43 | 0 | 35.83% | 10000 | 0 | Academic | Central
| 119 | 04.758 | 1 | Humanities Fine Arts | Morris | 121 | Hand-wash Sinks | The plumbing fixtures include stainless steel and porcelain hand-wash sinks. | 1972 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2007 | 2026 | 1 | 2 | Each | 977.9 | 1.25 | 1.3 | 1.25 | 1 | 3178.18 | D201004 | Sinks | Sinks | Life Cycle Replacement | Active | Replace Sinks | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 977.9 | 3972.72 | 0 | 50000% | 10000 | 0 | Academic | Central
| 114 | 04.758 | 1 | Humanities Fine Arts | Morris | 116 | Handwash & Kitchen Sinks | The plumbing fixtures include stainless steel handwash and kitchen sinks. | 1972 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2007 | 2026 | 1 | 2 | Each | 977.9 | 1.25 | 1.3 | 1.25 | 1 | 3178.18 | D201004 | Sinks | Sinks | Life Cycle Replacement | Active | Replace Sinks | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 977.9 | 3972.72 | 0 | 50000% | 10000 | 0 | Academic | Central
| 842 | 04.758 | 1 | Humanities Fine Arts | Morris | 9 | Heat Exchangers | The HVAC system is provided with plate & frame heat exchangers. | 2012 | 2019-10-15 | 3 - Fair | Repair good shape | 30 | 2042 | 2031 | 6 | 2700 | MBH | 56.21 |  | 1.3 | 1.25 | 1.49 | 367465.85 | D302011 | Steam Boilers - Over 1000 MBH | Rebuild | Major Repair | Active | Rebuild | Priority 5: Upgrade | 86 | 2026 |  |  |  | 15000 | 0 | - | 0 | 0 | Academic | Central
| 19 | 04.758 | 1 | Humanities Fine Arts | Morris | 17 | Humidity Control Equipment - Steam Humidification | The HVAC system is equipped with a steam humidification system which supply humidification to the Trane air handler. | 1998 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2018 | 2026 | 1 | 1 | Each | 4679.29 | 1.25 | 1.3 | 1.25 | 1 | 7603.85 | D304061 | Fuel-Fired Humidifiers | Fuel-Fired Humidifiers | Life Cycle Replacement | Active | Replace Fuel-Fired Humidifiers | Priority 3: Imminent Breakdown | 0 | 2026 | 1 | Each | 4679.29 | 9504.81 | 1 | 100000% | 10000 | 0 | Academic | Central
| 86 | 04.758 | 1 | Humanities Fine Arts | Morris | 85 | Humidity Control Equipment - Steam Humidification | The HVAC system is equipped with a NORTEC steam humidification unit for AHU-1. | 1997 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2017 | 2026 | 1 | 1 | Each | 4679.29 | 1.25 | 1.3 | 1.25 | 1 | 7603.85 | D304061 | Fuel-Fired Humidifiers | Fuel-Fired Humidifiers | Life Cycle Replacement | Active | Replace Fuel-Fired Humidifiers | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 4679.29 | 9504.81 | 0 | 100000% | 10000 | 0 | Academic | Central
| 104 | 04.758 | 1 | Humanities Fine Arts | Morris | 105 | Humidity Control Equipment - Steam Humidification | The HVAC system is equipped with a NORTEC steam humidification unit which supplys humidification to the main 2,0000 CFM air handler. | 1998 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2018 | 2026 | 1 | 1 | Each | 4679.29 | 1.25 | 1.3 | 1.25 | 1 | 7603.85 | D304061 | Fuel-Fired Humidifiers | Fuel-Fired Humidifiers | Life Cycle Replacement | Active | Replace Fuel-Fired Humidifiers | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 4679.29 | 9504.81 | 0 | 100000% | 10000 | 0 | Academic | Central
| 61 | 04.758 | 1 | Humanities Fine Arts | Morris | 60 | Lighting Fixtures - Exterior | The exterior lighting system consists of recessed mounted fixtures around the perimeter of the building. | 2000 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2035 | 2026 | 1 | 1500 | SF | 2.65 | 1.25 | 1.3 | 1.25 | 1 | 6459.38 | D502021 | Interior Lighting (Residential) | Interior Lighting (Residential) | Life Cycle Replacement | Active | Replace Interior Lighting (Residential) | Priority 4: Proactive Replacement | 0 | 2026 | 1500 | SF | 2.65 | 8074.22 | 0 | 66.67% | 10000 | 0 | Academic | Central
| 72 | 04.758 | 1 | Humanities Fine Arts | Morris | 71 | Lighting Fixtures - Exterior | The exterior lighting system consists of surface and recessed mounted fixtures, conduit and wire. | 2000 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2035 | 2026 | 1 | 2000 | SF | 2.65 | 1.25 | 1.3 | 1.25 | 1 | 8612.5 | D502021 | Interior Lighting (Residential) | Interior Lighting (Residential) | Life Cycle Replacement | Active | Replace Interior Lighting (Residential) | Priority 4: Proactive Replacement | 0 | 2026 | 2000 | SF | 2.65 | 10765.63 | 0 | 50% | 10000 | 0 | Academic | Central
| 36 | 04.758 | 1 | Humanities Fine Arts | Morris | 34 | Painted Floor Finish | The building's floor finishes include painted floor finish located at 500 floor storage room and electrical rooms. | 2010 | 2019-10-15 | 2 - Good | The painted floor finish is in good condition overall, lifecycle replacement can be deferred. | 15 | 2025 | 2026 | 1 | 852 | SF | 3.65 | 1.25 | 1.3 | 1.25 | 1 | 5053.43 | C302007 | Painted / Sealed Floor | Painted / Sealed Floor | Life Cycle Replacement | Active | Replace Painted / Sealed Floor | Priority 4: Proactive Replacement | 31 | 2026 | 852 | SF | 3.65 | 6316.78 | 1 | 117.37% | 10000 | 0 | Academic | Central
| 48 | 04.758 | 1 | Humanities Fine Arts | Morris | 47 | Split DX Ductless Unit - 1.5 Tons | Cooling for the rock storage room is provided from an LG, 1.5 ton, split DX, condensing unit. | 2008 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2026 | 2026 | 1 | 1 | Each | 3743.74 | 1.25 | 1.3 | 1.25 | 1.5 | 9125.37 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 3743.74 | 11406.71 | 0 | 100000% | 10000 | 0 | Academic | Central
| 49 | 04.758 | 1 | Humanities Fine Arts | Morris | 48 | Split DX Ductless Unit - 2 Tons | Cooling for the rock storage room is provided from a CARRIER, 2 ton, split DX, condensing unit. | 2008 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2026 | 2026 | 1 | 2 | Each | 3743.74 | 1.25 | 1.3 | 1.25 | 1 | 12167.16 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 3743.74 | 15208.94 | 0 | 50000% | 10000 | 0 | Academic | Central
| 121 | 04.758 | 1 | Humanities Fine Arts | Morris | 123 | Steel framed guardrails | The building includes steel framed guardrails located on the 300 floor | 1982 | 2019-10-15 | 2 - Good | The guardrails are in fair condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 25 | 2007 | 2026 | 1 | 26 | LF | 298.06 | 1.25 | 1.3 | 1.25 | 1 | 12593.04 | B201007 | Exterior Guards and Railings | Exterior Guards and Railings | Life Cycle Replacement | Active | Replace Exterior Guards and Railings | Priority 4: Proactive Replacement | 44 | 2026 | 26 | LF | 298.06 | 15741.29 | 0 | 3846.15% | 10000 | 0 | Academic | Central
| 57 | 04.758 | 1 | Humanities Fine Arts | Morris | 56 | Sump Pump - Submersible - 1/2 HP | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 15 | 2012 | 2026 | 1 | 1 | Each | 4889.5 | 1.25 | 1.3 | 1.25 | 1 | 7945.44 | D203006 | Sanitary Waste Ejector Pump Systems | Sanitary Waste Ejector Pump Systems | Life Cycle Replacement | Active | Replace Sanitary Waste Ejector Pump Systems | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 4889.5 | 9931.8 | 0 | 100000% | 10000 | 0 | Academic | Central
| 55 | 04.758 | 1 | Humanities Fine Arts | Morris | 54 | Terrazzo Flooring - Cast In Place | The building's floor finish includes terrazzo floor finish. | 1972 | 2019-10-15 | 2 - Good | The floor finish is in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 50 | 2022 | 2026 | 1 | 183 | SF | 39.13 | 1.25 | 1.3 | 1.25 | 1 | 11636.28 | C302002 | Terrazzo Floor | Terrazzo Floor | Life Cycle Replacement | Active | Replace Terrazzo Floor | Priority 4: Proactive Replacement | 31 | 2026 | 183 | SF | 39.13 | 14545.35 | 0 | 546.45% | 10000 | 0 | Academic | Central
| 87 | 04.758 | 1 | Humanities Fine Arts | Morris | 86 | Unit Heaters | Heating for the loading dock and Main Electrical Vault is provided by suspended, electric, unit heaters. | 1997 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2027 | 2026 | 1 | 3 | Each | 2933.7 | 1.25 | 1.3 | 1.25 | 1 | 14301.79 | D305002 | Unit Heaters (Hydronic) | Unit Heaters (Hydronic) | Life Cycle Replacement | Active | Replace Unit Heaters (Hydronic) | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 2933.7 | 17877.23 | 0 | 33333.33% | 10000 | 0 | Academic | Central
| 50 | 04.758 | 1 | Humanities Fine Arts | Morris | 49 | Unit Heaters - Electric | Heating for the rock storage area is provided by a suspended, electric, unit heater. | 1997 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2027 | 2026 | 1 | 1 | Each | 2933.7 | 1.25 | 1.3 | 1.25 | 1 | 4767.26 | D305002 | Unit Heaters (Hydronic) | Unit Heaters (Hydronic) | Life Cycle Replacement | Active | Replace Unit Heaters (Hydronic) | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 2933.7 | 5959.08 | 0 | 100000% | 10000 | 0 | Academic | Central
| 96 | 04.758 | 1 | Humanities Fine Arts | Morris | 96 | Unit Heaters - Electric | Heating for the boiler room and the Main Electrical Vault is each provided by a suspended electric unit heater. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2020 | 2026 | 1 | 2 | Each | 2933.7 | 1.25 | 1.3 | 1.25 | 1 | 9534.53 | D305002 | Unit Heaters (Hydronic) | Unit Heaters (Hydronic) | Life Cycle Replacement | Active | Replace Unit Heaters (Hydronic) | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 2933.7 | 11918.16 | 0 | 50000% | 10000 | 0 | Academic | Central
| 71 | 04.758 | 1 | Humanities Fine Arts | Morris | 70 | Unit Heaters - Electric (Each) | Heating for the rock storage area is provided by a suspended, electric, unit heater. | 1985 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2015 | 2026 | 1 | 1 | Each | 2933.7 | 1.25 | 1.3 | 1.25 | 1 | 4767.26 | D305002 | Unit Heaters (Hydronic) | Unit Heaters (Hydronic) | Life Cycle Replacement | Active | Replace Unit Heaters (Hydronic) | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 2933.7 | 5959.08 | 0 | 100000% | 10000 | 0 | Academic | Central
| 105 | 04.758 | 1 | Humanities Fine Arts | Morris | 106 | Unit Heaters - Hot Water | Space heating in mechanical roooms is provided by suspended, forced hot water unit heaters. | 1994 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2024 | 2026 | 1 | 2 | Each | 2933.7 | 1.25 | 1.3 | 1.25 | 1 | 9534.53 | D305002 | Unit Heaters (Hydronic) | Unit Heaters (Hydronic) | Life Cycle Replacement | Active | Replace Unit Heaters (Hydronic) | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 2933.7 | 11918.16 | 0 | 50000% | 10000 | 0 | Academic | Central
| 116 | 04.758 | 1 | Humanities Fine Arts | Morris | 118 | Walk-in Coolers and Freezers | The building is provided with walk-in coolers and freezers. | 1997 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2027 | 2026 | 1 | 2 | Each | 4679.29 | 1.25 | 1.3 | 1.25 | 1 | 15207.69 | E109002 | Basketball Backboards - Fixed | Basketball Backboards - Fixed | Life Cycle Replacement | Active | Replace Basketball Backboards - Fixed | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 4679.29 | 19009.62 | 0 | 50000% | 10000 | 0 | Academic | Central
| 38 | 04.758 | 1 | Humanities Fine Arts | Morris | 36 | Water Coolers | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2020 | 2026 | 1 | 3 | Each | 1404.48 | 1.25 | 1.3 | 1.25 | 1 | 6846.84 | D201007 | Bidets | Bidets | Life Cycle Replacement | Active | Replace Bidets | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 1404.48 | 8558.55 | 0 | 33333.33% | 10000 | 0 | Academic | Central
| 44 | 04.758 | 1 | Humanities Fine Arts | Morris | 43 | Water Coolers | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1995 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2025 | 2026 | 1 | 3 | Each | 1404.48 | 1.25 | 1.3 | 1.25 | 1 | 6846.84 | D201007 | Bidets | Bidets | Life Cycle Replacement | Active | Replace Bidets | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 1404.48 | 8558.55 | 0 | 33333.33% | 10000 | 0 | Academic | Central
| 60 | 04.758 | 1 | Humanities Fine Arts | Morris | 59 | Water Coolers | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2020 | 2026 | 1 | 3 | Each | 1404.48 | 1.25 | 1.3 | 1.25 | 1 | 6846.84 | D201007 | Bidets | Bidets | Life Cycle Replacement | Active | Replace Bidets | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 1404.48 | 8558.55 | 0 | 33333.33% | 10000 | 0 | Academic | Central
| 68 | 04.758 | 1 | Humanities Fine Arts | Morris | 67 | Water Coolers | Plumbing fixtures include wall mounted stainless steel water coolers on each floor. | 1990 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2020 | 2026 | 1 | 4 | Each | 1404.48 | 1.25 | 1.3 | 1.25 | 1 | 9129.12 | D201007 | Bidets | Bidets | Life Cycle Replacement | Active | Replace Bidets | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Each | 1404.48 | 11411.4 | 0 | 25000% | 10000 | 0 | Academic | Central
| 120 | 04.758 | 1 | Humanities Fine Arts | Morris | 122 | Water Fountains | The plumbing fixtures includes stainless steel water fountains. | 1982 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2012 | 2026 | 1 | 6 | Each | 1466.85 | 1.25 | 1.3 | 1.25 | 1 | 14301.79 | D201006 | Drinking Water Fountains (Non-refrigerated) | Drinking Water Fountains (Non-refrigerated) | Life Cycle Replacement | Active | Replace Drinking Water Fountains (Non-refrigerated) | Priority 4: Proactive Replacement | 0 | 2026 | 6 | Each | 1466.85 | 17877.23 | 0 | 16666.67% | 10000 | 0 | Academic | Central
| 148 | 03.523 | 2 | Kirby Student Ctr | Duluth | 158 | Carpet Tile Flooring | The building's floor finishes include carpet floor tiles located in the 200 floor. | 2005 | 2019-11-07 | 2 - Good | The carpet tiles are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 10 | 2015 | 2026 | 1 | 1830 | SF | 7.87 | 1.25 | 1.3 | 1.05 | 1 | 19658.87 | C302005 | Carpet Floor | Carpet Floor | Life Cycle Replacement | Active | Replace Carpet Floor | Priority 4: Proactive Replacement | 28 | 2026 | 1830 | SF | 7.87 | 24573.58 | 0 | 54.64% | 10000 | 0 | Operations | North
| 167 | 03.523 | 2 | Kirby Student Ctr | Duluth | 178 | Distribution Equipment - Motor Control Centre | The electrical distribution system for the building includes a motor control centre for the supply and control of electrical power to HVAC equipment and other motor loads. | 1985 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2025 | 2026 | 1 | 1 | Each | 12166.77 | 1.25 | 1.3 | 1.05 | 1 | 16607.64 | D501024 | Main Service Panels | Main Service Panels | Life Cycle Replacement | Active | Replace Main Service Panels | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 12166.77 | 20759.55 | 0 | 100000% | 10000 | 0 | Operations | North
| 161 | 03.523 | 2 | Kirby Student Ctr | Duluth | 172 | Distribution Equipment - Motor Control Centres | The electrical distribution system for the building includes motor control centres for the supply and control of electrical power to HVAC equipment and other motor loads. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 12166.77 | 1.25 | 1.3 | 1.05 | 1 | 16607.64 | D501024 | Main Service Panels | Main Service Panels | Life Cycle Replacement | Active | Replace Main Service Panels | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 12166.77 | 20759.55 | 0 | 100000% | 10000 | 0 | Operations | North
| 149 | 03.523 | 2 | Kirby Student Ctr | Duluth | 159 | Eggcrate Ceiling - Exposed T-bar | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 2019-11-07 | 2 - Good | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 1991 | SF | 7.87 | 1.25 | 1.3 | 1.05 | 1 | 21388.42 | C303007 | Suspended Acoustic Ceiling Panels | Suspended Acoustic Ceiling Panels | Life Cycle Replacement | Active | Replace Suspended Acoustic Ceiling Panels | Priority 4: Proactive Replacement | 28 | 2026 | 1991 | SF | 7.87 | 26735.52 | 0 | 50.23% | 10000 | 0 | Operations | North
| 162 | 03.523 | 2 | Kirby Student Ctr | Duluth | 173 | Emergency Battery Pack Lights | The emergency lighting system includes self-contained battery packs and lights. | 2000 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2020 | 2026 | 1 | 27857 | SF Building | 0.5 | 1.25 | 1.3 | 1.05 | 1 | 19012.4 | D509003 | Emergency Lighting Systems | Emergency Lighting Systems | Life Cycle Replacement | Active | Replace Emergency Lighting Systems | Priority 4: Proactive Replacement | 0 | 2026 | 27857 | SF Building | 0.5 | 23765.5 | 0 | 3.59% | 10000 | 0 | Operations | North
| 152 | 03.523 | 2 | Kirby Student Ctr | Duluth | 162 | Exhaust System - Fans - General Building | The HVAC system includes centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1997 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2022 | 2026 | 1 | 4 | Each | 2808.19 | 1.25 | 1.3 | 1.05 | 1 | 15332.72 | D304031 | Exhaust Fans - Centrifugal | Exhaust Fans - Centrifugal | Life Cycle Replacement | Active | Replace Exhaust Fans - Centrifugal | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Each | 2808.19 | 19165.9 | 0 | 25000% | 10000 | 0 | Operations | North
| 173 | 03.523 | 2 | Kirby Student Ctr | Duluth | 185 | Exterior Storefront Door - Double Leaf | The exterior doors consist of aluminum framed glazed double -doors mounted by butt hinges to aluminum door frames. | 1994 | 2019-11-07 | 2 - Good | The exterior doors are in good condition overall, lifecycle replacement can be deferred. | 35 | 2029 | 2026 | 1 | 1 | Each | 8423.03 | 1.25 | 1.3 | 1.05 | 1 | 11497.44 | B203028 | Exterior - Double Door - Aluminum and Glass | Exterior - Double Door - Aluminum and Glass | Life Cycle Replacement | Active | Replace Exterior - Double Door - Aluminum and Glass | Priority 4: Proactive Replacement | 31 | 2026 | 1 | Each | 8423.03 | 14371.79 | 0 | 100000% | 10000 | 0 | Operations | North
| 154 | 03.523 | 2 | Kirby Student Ctr | Duluth | 164 | Fixed Casework - Lab Benches | The building includes metal lab benches with acid resistant countertops. | 1972 | 2019-11-07 | 2 - Good | The lab benches are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred | 25 | 1997 | 2026 | 1 | 1776 | SF Building | 5.22 | 1.25 | 1.3 | 1.05 | 1 | 12654.53 | C103011 | Millwork General | Millwork General | Life Cycle Replacement | Active | Replace Millwork General | Priority 4: Proactive Replacement | 28 | 2026 | 1776 | SF Building | 5.22 | 15818.17 | 0 | 56.31% | 10000 | 0 | Operations | North
| 138 | 03.523 | 2 | Kirby Student Ctr | Duluth | 148 | Interior Automatic Openers - Single | The building includes interior doors with automatic openers for single swing doors located in 400 floor office area. | 2005 | 2019-11-07 | 2 - Good | The door openers are functioning as intended, lifecycle replacement can be deferred. | 15 | 2020 | 2026 | 1 | 3 | Each | 3743.74 | 1.25 | 1.3 | 1.05 | 1 | 15330.62 | C102007 | Interior - Automatic Door Openers | Interior - Automatic Door Openers | Life Cycle Replacement | Active | Replace Interior - Automatic Door Openers | Priority 4: Proactive Replacement | 28 | 2026 | 3 | Each | 3743.74 | 19163.27 | 0 | 33333.33% | 10000 | 0 | Operations | North
| 165 | 03.523 | 2 | Kirby Student Ctr | Duluth | 176 | Interior Overhead Rolling Doors - 10' x 10' | The building includes a sectional overhead door that is automatically operated located in the 200 floor kitchen. | 1972 | 2019-11-07 | 2 - Good | The interior door is in good condition overall and functioning as intended. lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 1 | Each | 11230.45 | 1.25 | 1.3 | 1.05 | 1 | 15329.56 | C102006 | Interior - Overhead Doors - Industrial | Interior - Overhead Doors - Industrial | Life Cycle Replacement | Active | Replace Interior - Overhead Doors - Industrial | Priority 4: Proactive Replacement | 28 | 2026 | 1 | Each | 11230.45 | 19161.96 | 0 | 100000% | 10000 | 0 | Operations | North
| 183 | 03.523 | 2 | Kirby Student Ctr | Duluth | 195 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 300 floor. | 1994 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Lifecycle replacement can be deferred. | 75 | 2069 | 2026 | 1 | 269 | SF | 52.22 | 1.25 | 1.3 | 1.05 | 1 | 19174.4 | C101005 | Interior Windows | Interior Windows | Life Cycle Replacement | Active | Replace Interior Windows | Priority 4: Proactive Replacement | 28 | 2026 | 269 | SF | 52.22 | 23968 | 0 | 371.75% | 10000 | 0 | Operations | North
| 172 | 03.523 | 2 | Kirby Student Ctr | Duluth | 183 | Lighting Fixtures - Exterior | The exterior lighting system consists of recessed mounted fixtures with CF lamps, conduit and wire. | 2000 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2035 | 2026 | 1 | 5000 | SF | 2.65 | 1.25 | 1.3 | 1.05 | 1 | 18086.25 | D502021 | Interior Lighting (Residential) | Interior Lighting (Residential) | Life Cycle Replacement | Active | Replace Interior Lighting (Residential) | Priority 4: Proactive Replacement | 0 | 2026 | 5000 | SF | 2.65 | 22607.81 | 0 | 20% | 10000 | 0 | Operations | North
| 156 | 03.523 | 2 | Kirby Student Ctr | Duluth | 166 | Single doors | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 2 | Each | 5615.61 | 1.25 | 1.3 | 1.05 | 1 | 15330.62 | C102024 | Interior - Double Door - Hollow Metal | Interior - Double Door - Hollow Metal | Life Cycle Replacement | Active | Replace Interior - Double Door - Hollow Metal | Priority 4: Proactive Replacement | 28 | 2026 | 2 | Each | 5615.61 | 19163.27 | 0 | 50000% | 10000 | 0 | Operations | North
| 137 | 03.523 | 2 | Kirby Student Ctr | Duluth | 147 | Soffit - Plaster on Metal Lath | The buildings overhang soffit is a plaster-on-metal lath soffit. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed on the exposed soffits. Lifecycle replacment can be deferred. | 50 | 2022 | 2026 | 1 | 1292 | SF | 9.59 | 1.25 | 1.3 | 1.05 | 1 | 16912.73 | B201008 | Exterior Soffits | Exterior Soffits | Life Cycle Replacement | Active | Replace Exterior Soffits | Priority 4: Proactive Replacement | 41 | 2026 | 1292 | SF | 9.59 | 21140.92 | 0 | 77.4% | 10000 | 0 | Operations | North
| 145 | 03.523 | 2 | Kirby Student Ctr | Duluth | 155 | Split Condensing Unit | Cooling for the some of the offices is provided from a split condensing unit having a cooling capacity of 3 tons. | 2008 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2026 | 2026 | 1 | 3 | Each | 3743.74 | 1.25 | 1.3 | 1.05 | 1 | 15330.62 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 3743.74 | 19163.27 | 0 | 33333.33% | 10000 | 0 | Operations | North
| 177 | 03.523 | 2 | Kirby Student Ctr | Duluth | 189 | Sump Pump - Submersible - 1/2 HP | The water drainage system includes duplex sanitary sump pump systems. | 2007 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Lifecycle replacement can be deferred. | 15 | 2022 | 2026 | 1 | 2 | Each | 4889.5 | 1.25 | 1.3 | 1.05 | 1 | 13348.34 | D203006 | Sanitary Waste Ejector Pump Systems | Sanitary Waste Ejector Pump Systems | Life Cycle Replacement | Active | Replace Sanitary Waste Ejector Pump Systems | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 4889.5 | 16685.42 | 0 | 50000% | 10000 | 0 | Operations | North
| 171 | 03.523 | 2 | Kirby Student Ctr | Duluth | 182 | Transformers - 30 KVA & 15 KVA | The electrical system is equipped with a 30 KVA, 600V - 208Y/120V transformer; and a 15 KVA, 600V - 208Y/120V transformer located in the Main Electrical Room. | 1982 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2032 | 2026 | 1 | 1 | Each | 9358.58 | 1.25 | 1.3 | 1.05 | 1 | 12774.46 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 9358.58 | 15968.08 | 0 | 100000% | 10000 | 0 | Operations | North
| 143 | 03.523 | 2 | Kirby Student Ctr | Duluth | 153 | Vinyl Tile Flooring - 2005 | The building's floor finishes include VCT floor finish. | 1997 | 2019-11-07 | 2 - Good | The vinyl tiles are in good condition overall, lifecycle replacement can be deferred. | 15 | 2012 | 2026 | 1 | 1464 | SF | 9.08 | 1.25 | 1.3 | 1.05 | 1 | 18145.11 | C302022 | Vinyl Tile / Plank Floor | Vinyl Tile / Plank Floor | Life Cycle Replacement | Active | Replace Vinyl Tile / Plank Floor | Priority 4: Proactive Replacement | 28 | 2026 | 1464 | SF | 9.08 | 22681.39 | 0 | 68.31% | 10000 | 0 | Operations | North
| 157 | 03.523 | 2 | Kirby Student Ctr | Duluth | 167 | Vinyl Tile Flooring - 2009 | The building's floor finish includes vinyl tiles located in the 300 floor. | 2009 | 2019-11-07 | 2 - Good | The vinyl tiles are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 15 | 2024 | 2026 | 1 | 1615 | SF | 9.08 | 1.25 | 1.3 | 1.05 | 1 | 20016.63 | C302022 | Vinyl Tile / Plank Floor | Vinyl Tile / Plank Floor | Life Cycle Replacement | Active | Replace Vinyl Tile / Plank Floor | Priority 4: Proactive Replacement | 28 | 2026 | 1615 | SF | 9.08 | 25020.79 | 0 | 61.92% | 10000 | 0 | Operations | North
| 181 | 03.523 | 2 | Kirby Student Ctr | Duluth | 193 | Walk-in Coolers and Freezers | The building is provided with walk-in coolers and freezers. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2002 | 2026 | 1 | 3 | Each | 4679.29 | 1.25 | 1.3 | 1.05 | 1 | 19161.69 | E109002 | Basketball Backboards - Fixed | Basketball Backboards - Fixed | Life Cycle Replacement | Active | Replace Basketball Backboards - Fixed | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 4679.29 | 23952.12 | 0 | 33333.33% | 10000 | 0 | Operations | North
| 170 | 03.523 | 2 | Kirby Student Ctr | Duluth | 181 | Water Coolers - Wall Mounted (Each) | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 2000 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2030 | 2026 | 1 | 8 | Each | 1404.48 | 1.25 | 1.3 | 1.05 | 1 | 15336.92 | D201007 | Bidets | Bidets | Life Cycle Replacement | Active | Replace Bidets | Priority 4: Proactive Replacement | 0 | 2026 | 8 | Each | 1404.48 | 19171.15 | 0 | 12500% | 10000 | 0 | Operations | North
| 151 | 03.523 | 2 | Kirby Student Ctr | Duluth | 161 | Water Heater - Elec - Residential - 143 Litre | Domestic hot water is provided from a 143 litre, SPACESAVER, electric, water heater rated at 3000 W. | 2010 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2030 | 2026 | 1 | 2 | Each | 5615.61 | 1.25 | 1.3 | 1.05 | 1 | 15330.62 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 5615.61 | 19163.27 | 0 | 50000% | 10000 | 0 | Operations | North
| 255 | 05.855 | 3 | Lysaker Gym | Crookston | 273 | Automatic door openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2000 | 2019-11-08 | 2 - Good | The door openers are in a fair condition overall, lifecycle replacement can be deferred. | 15 | 2015 | 2026 | 1 | 4 | Each | 3743.74 | 1.25 | 1.3 | 1.15 | 1 | 22387.57 | B203008 | Exterior - Automatic Door Openers | Exterior - Automatic Door Openers | Life Cycle Replacement | Active | Replace Exterior - Automatic Door Openers | Priority 4: Proactive Replacement | 21 | 2026 | 4 | Each | 3743.74 | 27984.46 | 0 | 25000% | 10000 | 0 | Athletics | East
| 227 | 05.855 | 3 | Lysaker Gym | Crookston | 242 | Carpet | The building's floor finishes include broadloom carpet located on the 300 floor. | 2005 | 2019-11-08 | 2 - Good | The carpet is in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 10 | 2015 | 2026 | 1 | 2422 | SF | 7.87 | 1.25 | 1.3 | 1.15 | 1 | 28496.4 | C302005 | Carpet Floor | Carpet Floor | Life Cycle Replacement | Active | Replace Carpet Floor | Priority 4: Proactive Replacement | 18 | 2026 | 2422 | SF | 7.87 | 35620.51 | 0 | 41.29% | 10000 | 0 | Athletics | East
| 199 | 05.855 | 3 | Lysaker Gym | Crookston | 213 | Condensing Unit | Cooling for the outside walk in cooler is provided by a 4 ton condensing unit. | 2008 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2026 | 2026 | 1 | 4 | Each | 3743.74 | 1.25 | 1.3 | 1.15 | 1 | 22387.57 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Each | 3743.74 | 27984.46 | 0 | 25000% | 10000 | 0 | Athletics | East
| 207 | 05.855 | 3 | Lysaker Gym | Crookston | 221 | Emergency Eyewash Units and Shower Units | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2025 | 2026 | 1 | 3 | Per Lavatory | 7487.48 | 1.25 | 1.3 | 1.15 | 1 | 33581.35 | D201022 | Universal/Gender Neutral Washroom Fixtures | Universal/Gender Neutral Washroom Fixtures | Life Cycle Replacement | Active | Replace Universal/Gender Neutral Washroom Fixtures | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Per Lavatory | 7487.48 | 41976.68 | 0 | 33333.33% | 10000 | 0 | Athletics | East
| 200 | 05.855 | 3 | Lysaker Gym | Crookston | 214 | Exhaust System - Fans - General Building | The HVAC exhaust ventilation system includes centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1998 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. There is damage to one fan, the sheet metal shroud should be repaired under normal maintenance. | 25 | 2023 | 2026 | 1 | 6 | Each | 2808.19 | 1.25 | 1.3 | 1.15 | 1 | 25189.46 | D304031 | Exhaust Fans - Centrifugal | Exhaust Fans - Centrifugal | Life Cycle Replacement | Active | Replace Exhaust Fans - Centrifugal | Priority 4: Proactive Replacement | 0 | 2026 | 6 | Each | 2808.19 | 31486.83 | 0 | 16666.67% | 10000 | 0 | Athletics | East
| 233 | 05.855 | 3 | Lysaker Gym | Crookston | 248 | Exhaust System - Fans - General Building | The HVAC exhaust ventilation system centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1990 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2015 | 2026 | 1 | 6 | Each | 2808.19 | 1.25 | 1.3 | 1.15 | 1 | 25189.46 | D304031 | Exhaust Fans - Centrifugal | Exhaust Fans - Centrifugal | Life Cycle Replacement | Active | Replace Exhaust Fans - Centrifugal | Priority 4: Proactive Replacement | 0 | 2026 | 6 | Each | 2808.19 | 31486.83 | 0 | 16666.67% | 10000 | 0 | Athletics | East
| 240 | 05.855 | 3 | Lysaker Gym | Crookston | 255 | Exhaust System - Fans - General Building | The HVAC system is provided with centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1994 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2019 | 2026 | 1 | 8 | Each | 2808.19 | 1.25 | 1.3 | 1.15 | 1 | 33585.95 | D304031 | Exhaust Fans - Centrifugal | Exhaust Fans - Centrifugal | Life Cycle Replacement | Active | Replace Exhaust Fans - Centrifugal | Priority 4: Proactive Replacement | 0 | 2026 | 8 | Each | 2808.19 | 41982.44 | 0 | 12500% | 10000 | 0 | Athletics | East
| 220 | 05.855 | 3 | Lysaker Gym | Crookston | 235 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1972 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 1997 | 2026 | 1 | 5 | Each | 4679.29 | 1.25 | 1.3 | 1.15 | 1 | 34977.69 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 5 | Each | 4679.29 | 43722.12 | 0 | 20000% | 10000 | 0 | Athletics | East
| 212 | 05.855 | 3 | Lysaker Gym | Crookston | 226 | Exit Signs | The building is provided with Exit Signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 1972 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2007 | 2026 | 1 | 800 | SF | 20.89 | 1.25 | 1.3 | 1.15 | 1 | 24984.44 | D502022 | Interior Lighting (Industrial) | Interior Lighting (Industrial) | Life Cycle Replacement | Active | Replace Interior Lighting (Industrial) | Priority 4: Proactive Replacement | 0 | 2026 | 800 | SF | 20.89 | 31230.55 | 0 | 125% | 10000 | 0 | Athletics | East
| 206 | 05.855 | 3 | Lysaker Gym | Crookston | 220 | Exterior Hollow Metal Door - Single Leaf | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 2019-11-08 | 2 - Good | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 5 | Each | 2995.3 | 1.25 | 1.3 | 1.15 | 1 | 22389.87 | B203023 | Exterior - Single Door - Hollow Metal | Exterior - Single Door - Hollow Metal | Life Cycle Replacement | Active | Replace Exterior - Single Door - Hollow Metal | Priority 4: Proactive Replacement | 21 | 2026 | 5 | Each | 2995.3 | 27987.33 | 0 | 20000% | 10000 | 0 | Athletics | East
| 218 | 05.855 | 3 | Lysaker Gym | Crookston | 232 | Exterior Storefront Door - Double Leaf | The exterior doors consist of hollow metal glazed double -doors mounted by butt hinges to metal frames. | 1972 | 2019-11-08 | 2 - Good | The exterior doors are in fair condition overall and functioning as intended. Lifecycle replacement can be deferred. | 35 | 2007 | 2026 | 1 | 2 | Each | 8423.03 | 1.25 | 1.3 | 1.15 | 1 | 25184.86 | B203028 | Exterior - Double Door - Aluminum and Glass | Exterior - Double Door - Aluminum and Glass | Life Cycle Replacement | Active | Replace Exterior - Double Door - Aluminum and Glass | Priority 4: Proactive Replacement | 21 | 2026 | 2 | Each | 8423.03 | 31481.07 | 0 | 50000% | 10000 | 0 | Athletics | East
| 235 | 05.855 | 3 | Lysaker Gym | Crookston | 250 | Exterior Storefront Door - Double Leaf | The exterior doors consist of glass metal framed double-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 1982 | 2019-11-08 | 2 - Good | The exterior doors are in fair condition overall, lifecycle replacement can be deferred. | 35 | 2017 | 2026 | 1 | 2 | Each | 8423.03 | 1.25 | 1.3 | 1.15 | 1 | 25184.86 | B203028 | Exterior - Double Door - Aluminum and Glass | Exterior - Double Door - Aluminum and Glass | Life Cycle Replacement | Active | Replace Exterior - Double Door - Aluminum and Glass | Priority 4: Proactive Replacement | 21 | 2026 | 2 | Each | 8423.03 | 31481.07 | 0 | 50000% | 10000 | 0 | Athletics | East
| 221 | 05.855 | 3 | Lysaker Gym | Crookston | 236 | Exterior Storefront Door - Single Leaf | The exterior doors consist of hollow metal glazed single -doors mounted by butt hinges to metal door frames. | 1972 | 2019-11-08 | 2 - Good | The exterior doors have aged but they are in a fair condition overall, life cycle replacement can be deferred. | 35 | 2007 | 2026 | 1 | 2 | Each | 8423.03 | 1.25 | 1.3 | 1.15 | 1 | 25184.86 | B203028 | Exterior - Double Door - Aluminum and Glass | Exterior - Double Door - Aluminum and Glass | Life Cycle Replacement | Active | Replace Exterior - Double Door - Aluminum and Glass | Priority 4: Proactive Replacement | 21 | 2026 | 2 | Each | 8423.03 | 31481.07 | 0 | 50000% | 10000 | 0 | Athletics | East
| 201 | 05.855 | 3 | Lysaker Gym | Crookston | 215 | Fan-coil Units | HVAC distribution includes a number of fan-coil units in the corridors near the entrances. | 1998 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2023 | 2026 | 1 | 4 | Each | 4889.5 | 1.25 | 1.3 | 1.15 | 1 | 29239.21 | D305003 | Fan Coil Units | Fan Coil Units | Life Cycle Replacement | Active | Replace Fan Coil Units | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Each | 4889.5 | 36549.01 | 0 | 25000% | 10000 | 0 | Athletics | East
| 224 | 05.855 | 3 | Lysaker Gym | Crookston | 239 | Gypsum Board Ceiling | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 2019-11-08 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 15 | 1987 | 2026 | 1 | 9042 | SF | 2.65 | 1.25 | 1.3 | 1.15 | 1 | 35822.14 | C303006 | Painted Ceiling Structures | Painted Ceiling Structures | Life Cycle Replacement | Active | Replace Painted Ceiling Structures | Priority 4: Proactive Replacement | 18 | 2026 | 9042 | SF | 2.65 | 44777.68 | 0 | 11.06% | 10000 | 0 | Athletics | East
| 202 | 05.855 | 3 | Lysaker Gym | Crookston | 216 | Interior Doors - Special | The building includes copper shielded doors locate on the 400 floor. | 1972 | 2019-11-08 | 2 - Good | The copper shielded doors are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 40 | 2012 | 2026 | 1 | 5 | Lump Sum | 3850 | 1.25 | 1.3 | 1.15 | 1 | 28778.75 | C102099 | Other Interior Doors | Other Interior Doors | Life Cycle Replacement | Active | Replace Other Interior Doors | Priority 4: Proactive Replacement | 18 | 2026 | 5 | Lump Sum | 3850 | 35973.44 | 0 | 20000% | 10000 | 0 | Athletics | East
| 215 | 05.855 | 3 | Lysaker Gym | Crookston | 229 | Lighting Fixtures - Exterior | The exterior lighting system includes wall mounted HID fixtures, around the perimeter of the building which includes conduit and wire. | 1990 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2025 | 2026 | 1 | 6500 | SF | 2.65 | 1.25 | 1.3 | 1.15 | 1 | 25751.38 | D502021 | Interior Lighting (Residential) | Interior Lighting (Residential) | Life Cycle Replacement | Active | Replace Interior Lighting (Residential) | Priority 4: Proactive Replacement | 0 | 2026 | 6500 | SF | 2.65 | 32189.22 | 0 | 15.38% | 10000 | 0 | Athletics | East
| 242 | 05.855 | 3 | Lysaker Gym | Crookston | 257 | Lighting Fixtures - Exterior | The exterior lighting system recessed mounted fixtures, lamps, conduit and wire. | 2000 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2035 | 2026 | 1 | 7000 | SF | 2.65 | 1.25 | 1.3 | 1.15 | 1 | 27732.25 | D502021 | Interior Lighting (Residential) | Interior Lighting (Residential) | Life Cycle Replacement | Active | Replace Interior Lighting (Residential) | Priority 4: Proactive Replacement | 0 | 2026 | 7000 | SF | 2.65 | 34665.31 | 0 | 14.29% | 10000 | 0 | Athletics | East
| 260 | 05.855 | 3 | Lysaker Gym | Crookston | 278 | Painted Concrete | The building&rsquo;s floor finishes include painted/sealed floor finish located in the Mechanical rooms. | 2007 | 2019-11-08 | 2 - Good | The painted floor finish is in excellent condition, no significant deficiencies were observed. | 15 | 2022 | 2026 | 1 | 4790 | SF | 3.65 | 1.25 | 1.3 | 1.15 | 1 | 26137.83 | C302007 | Painted / Sealed Floor | Painted / Sealed Floor | Life Cycle Replacement | Active | Replace Painted / Sealed Floor | Priority 4: Proactive Replacement | 18 | 2026 | 4790 | SF | 3.65 | 32672.29 | 0 | 20.88% | 10000 | 0 | Athletics | East
| 258 | 05.855 | 3 | Lysaker Gym | Crookston | 276 | Roof top stairs | The building includes wood framed stairs that provide access to the fume hoods. | 1982 | 2019-11-08 | 2 - Good | The stairs have aged but are functioning as intended. Lifecycle replacement can be deferred. | 40 | 2022 | 2026 | 1 | 20 | Per Riser | 936.32 | 1.25 | 1.3 | 1.15 | 1 | 27995.97 | C201002 | Exterior (Attached) Stair Construction | Exterior (Attached) Stair Construction | Life Cycle Replacement | Active | Replace Exterior (Attached) Stair Construction | Priority 4: Proactive Replacement | 28 | 2026 | 20 | Per Riser | 936.32 | 34994.96 | 0 | 5000% | 10000 | 0 | Athletics | East
| 835 | 05.855 | 3 | Lysaker Gym | Crookston | 203 | Small Lower Roofs | Built-up roofing with black rubberized flood coat and black aggregate surfacing system on the small lower roofs. | 2012 | 2019-11-08 | 1 - Excellent | The lower roof is good condition, no deficiencies were observed or reported. | 20 | 2032 | 2032 | 7 | 1378 | SF | 16.1 |  | 1.3 | 1.15 | 1 | 33167.77 | B301023 | Conventional - Single Ply Membrane | Clean Roof Drains | Preventative Maintenance | Active | PM | Priority 4: Proactive Replacement | 48 | 2026 |  |  |  | 1000 | 0 | - | 10000 | 0 | Athletics | East
| 211 | 05.855 | 3 | Lysaker Gym | Crookston | 225 | Transformer - 45 KVA | The building is equipped with a 45 kVA, 600V - 208Y/120V, 3-Phase, transformer on each floor. | 1972 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 2 | Each | 9358.58 | 1.25 | 1.3 | 1.15 | 1 | 27982.15 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 9358.58 | 34977.69 | 0 | 50000% | 10000 | 0 | Athletics | East
| 214 | 05.855 | 3 | Lysaker Gym | Crookston | 228 | Transformers - 45 KVA - 1972 | The building is equipped with a 45 KVA, 600V - 208Y/120V transformer on each floor. | 1972 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 2 | Each | 9358.58 | 1.25 | 1.3 | 1.15 | 1 | 27982.15 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 9358.58 | 34977.69 | 0 | 50000% | 10000 | 0 | Athletics | East
| 219 | 05.855 | 3 | Lysaker Gym | Crookston | 233 | Vinyl Tile Flooring | The building's floor finish includes asbestos containing vinyl tiles. | 1972 | 2019-11-08 | 2 - Good | The vinyl tiles are in fair condition overall, lifecycle replacement can be deferred. Cost includes a factor for abatement. | 15 | 1987 | 2026 | 1 | 1399 | SF | 9.08 | 1.25 | 1.3 | 1.15 | 1.5 | 28486.3 | C302022 | Vinyl Tile / Plank Floor | Vinyl Tile / Plank Floor | Life Cycle Replacement | Active | Replace Vinyl Tile / Plank Floor | Priority 4: Proactive Replacement | 18 | 2026 | 1399 | SF | 9.08 | 35607.87 | 0 | 71.48% | 10000 | 0 | Athletics | East
| 259 | 05.855 | 3 | Lysaker Gym | Crookston | 277 | Vinyl Tiles | The building's floor finishes include vinyl tiles located in room J205 and 300 floor corridor. | 2009 | 2019-11-08 | 2 - Good | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 15 | 2024 | 2026 | 1 | 2196 | SF | 9.08 | 1.25 | 1.3 | 1.15 | 1 | 29809.82 | C302022 | Vinyl Tile / Plank Floor | Vinyl Tile / Plank Floor | Life Cycle Replacement | Active | Replace Vinyl Tile / Plank Floor | Priority 4: Proactive Replacement | 18 | 2026 | 2196 | SF | 9.08 | 37262.28 | 0 | 45.54% | 10000 | 0 | Athletics | East
| 204 | 05.855 | 3 | Lysaker Gym | Crookston | 218 | Water Heater - Elec - 85 Gal | The domestic hot water is provided from a RHEEM, 322-Liter (85-gallon), electric, water heater rated at 24000 W. | 2006 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2026 | 2026 | 1 | 3 | Each | 5615.61 | 1.25 | 1.3 | 1.15 | 1 | 25186.01 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 5615.61 | 31482.51 | 0 | 33333.33% | 10000 | 0 | Athletics | East
| 246 | 05.855 | 3 | Lysaker Gym | Crookston | 261 | Water Heater - Gas - 76 Gallon | The domestic hot water is provided by a 288L (76-gal), John Wood, gas fired, water heater rated at 72MBH. | 2012 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2032 | 2026 | 1 | 3 | Each | 5615.61 | 1.25 | 1.3 | 1.15 | 1 | 25186.01 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 5615.61 | 31482.51 | 0 | 33333.33% | 10000 | 0 | Athletics | East
| 286 | 01.074 | 4 | Mayo Building | Minneapolis | 308 | Carpet Tile Flooring | The building's floor finishes include carpet tiles located in the offices. | 2015 | 2019-10-16 | 2 - Good | The carpet tiles are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 10 | 2025 | 2026 | 1 | 5242 | SF | 7.87 | 1.25 | 1.3 | 1 | 1 | 53630.9 | C302005 | Carpet Floor | Carpet Floor | Life Cycle Replacement | Active | Replace Carpet Floor | Priority 4: Proactive Replacement | 32 | 2026 | 5242 | SF | 7.87 | 67038.63 | 0 | 19.08% | 10000 | 0 | Academic | East
| 337 | 01.074 | 4 | Mayo Building | Minneapolis | 363 | Carpet tiles | The building includes carpet tile flooring located on the 300 floor | 2014 | 2019-10-16 | 2 - Good | The carpet tiles are in good condition overall, lifecycle replacement can be deferred. | 10 | 2024 | 2026 | 1 | 3552 | SF | 7.87 | 1.25 | 1.3 | 1 | 1 | 36340.51 | C302005 | Carpet Floor | Carpet Floor | Life Cycle Replacement | Active | Replace Carpet Floor | Priority 4: Proactive Replacement | 32 | 2026 | 3552 | SF | 7.87 | 45425.64 | 0 | 28.15% | 10000 | 0 | Academic | East
| 339 | 01.074 | 4 | Mayo Building | Minneapolis | 365 | Carpet tiles | The buildings floor finishes include carpet tiles located in pond inlet hall. | 2016 | 2019-10-16 | 2 - Good | The carpet tiles are in good condition overall, no deficiencies were observed. | 10 | 2026 | 2026 | 1 | 3563 | SF | 7.87 | 1.25 | 1.3 | 1 | 1 | 36453.05 | C302005 | Carpet Floor | Carpet Floor | Life Cycle Replacement | Active | Replace Carpet Floor | Priority 4: Proactive Replacement | 32 | 2026 | 3563 | SF | 7.87 | 45566.32 | 0 | 28.07% | 10000 | 0 | Academic | East
| 271 | 01.074 | 4 | Mayo Building | Minneapolis | 293 | Communal Washrooms | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 1998 | 2019-10-16 | 2 - Good | The washrooms are in fair condition, lifecycle replacement can be deferred. | 25 | 2023 | 2026 | 1 | 1 | Per Lavatory | 23396.45 | 1.25 | 1.3 | 1 | 1 | 30415.39 | C104021 | Communal Washroom Refurbishment | Communal Washroom Refurbishment | Life Cycle Replacement | Active | Replace Communal Washroom Refurbishment | Priority 4: Proactive Replacement | 32 | 2026 | 1 | Per Lavatory | 23396.45 | 38019.23 | 0 | 100000% | 10000 | 0 | Academic | East
| 338 | 01.074 | 4 | Mayo Building | Minneapolis | 364 | Distribution Transformer - 300kVA | The electrical system for the building is provided with a 300kVA, 600V - 208Y/120V, 3-Phase transformer. | 1972 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 4 | Each | 9358.58 | 1.25 | 1.3 | 1 | 1 | 48664.62 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Each | 9358.58 | 60830.77 | 0 | 25000% | 10000 | 0 | Academic | East
| 276 | 01.074 | 4 | Mayo Building | Minneapolis | 298 | Domestic Water Tank - 435 Litre | The domestic hot water is provided from a 435 liter, Rheem Rhuud, domestic cold water storage tank. | 2010 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2030 | 2026 | 1 | 5 | Each | 5615.61 | 1.25 | 1.3 | 1 | 1 | 36501.47 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 5 | Each | 5615.61 | 45626.83 | 0 | 20000% | 10000 | 0 | Academic | East
| 324 | 01.074 | 4 | Mayo Building | Minneapolis | 349 | DX Condensing Units | Cooling medium is provided by three condensing units, CU-1, CU-2 & CU-3, each having a cooling capacity of 2.5 tons. | 2007 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2025 | 2026 | 1 | 8 | Each | 3743.74 | 1.25 | 1.3 | 1 | 1 | 38934.9 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 8 | Each | 3743.74 | 48668.62 | 0 | 12500% | 10000 | 0 | Academic | East
| 274 | 01.074 | 4 | Mayo Building | Minneapolis | 296 | Emergency Eyewash Units | Plumbing fixtures include emergency safety eyewash and shower stations installed throughout the building in the labs. | 1998 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2023 | 2026 | 1 | 4 | Per Lavatory | 7487.48 | 1.25 | 1.3 | 1 | 1 | 38934.9 | D201022 | Universal/Gender Neutral Washroom Fixtures | Universal/Gender Neutral Washroom Fixtures | Life Cycle Replacement | Active | Replace Universal/Gender Neutral Washroom Fixtures | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Per Lavatory | 7487.48 | 48668.62 | 0 | 25000% | 10000 | 0 | Academic | East
| 297 | 01.074 | 4 | Mayo Building | Minneapolis | 319 | Emergency Eyewash Units and Shower Units | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2025 | 2026 | 1 | 4 | Per Lavatory | 7487.48 | 1.25 | 1.3 | 1 | 1 | 38934.9 | D201022 | Universal/Gender Neutral Washroom Fixtures | Universal/Gender Neutral Washroom Fixtures | Life Cycle Replacement | Active | Replace Universal/Gender Neutral Washroom Fixtures | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Per Lavatory | 7487.48 | 48668.62 | 0 | 25000% | 10000 | 0 | Academic | East
| 287 | 01.074 | 4 | Mayo Building | Minneapolis | 309 | Epoxy Flooring | The building's floor finishes include epoxy floor finish located in the laboratories. | 2000 | 2019-10-16 | 2 - Good | The floor finish is in good condition overall, lifecycle replacement can be deferred. | 15 | 2015 | 2026 | 1 | 9688 | SF | 3.65 | 1.25 | 1.3 | 1 | 1 | 45969.56 | C302007 | Painted / Sealed Floor | Painted / Sealed Floor | Life Cycle Replacement | Active | Replace Painted / Sealed Floor | Priority 4: Proactive Replacement | 32 | 2026 | 9688 | SF | 3.65 | 57461.95 | 0 | 10.32% | 10000 | 0 | Academic | East
| 298 | 01.074 | 4 | Mayo Building | Minneapolis | 320 | Exhaust System - Fans - General Building | The HVAC system is provided with centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1997 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2022 | 2026 | 1 | 12 | Each | 2808.19 | 1.25 | 1.3 | 1 | 1 | 43807.76 | D304031 | Exhaust Fans - Centrifugal | Exhaust Fans - Centrifugal | Life Cycle Replacement | Active | Replace Exhaust Fans - Centrifugal | Priority 4: Proactive Replacement | 0 | 2026 | 12 | Each | 2808.19 | 54759.71 | 0 | 8333.33% | 10000 | 0 | Academic | East
| 277 | 01.074 | 4 | Mayo Building | Minneapolis | 299 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. Note: System cost represents a 6 foot long fume hood. | 1998 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2023 | 2026 | 1 | 8 | Each | 4679.29 | 1.25 | 1.3 | 1 | 1 | 48664.62 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 8 | Each | 4679.29 | 60830.77 | 0 | 12500% | 10000 | 0 | Academic | East
| 291 | 01.074 | 4 | Mayo Building | Minneapolis | 313 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | The HVAC ventilation system for the labs includes constant volume fume hood exhaust systems with ducting. | 1990 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2015 | 2026 | 1 | 7 | Each | 4679.29 | 1.25 | 1.3 | 1 | 1 | 42581.54 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 7 | Each | 4679.29 | 53226.92 | 0 | 14285.71% | 10000 | 0 | Academic | East
| 315 | 01.074 | 4 | Mayo Building | Minneapolis | 337 | Exterior Storefront Door - Single Leaf | The exterior doors consist of glass metal framed single-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 1982 | 2019-10-16 | 2 - Good | The exterior doors are in fair condition overall, lifecycle replacement can be deferred. | 25 | 2007 | 2026 | 1 | 4 | Lump Sum | 7700 | 1.25 | 1.3 | 1 | 1 | 40040 | B203005 | Exterior - Hangar Doors | Exterior - Hangar Doors | Life Cycle Replacement | Active | Replace Exterior - Hangar Doors | Priority 4: Proactive Replacement | 35 | 2026 | 4 | Lump Sum | 7700 | 50050 | 0 | 25000% | 10000 | 0 | Academic | East
| 284 | 01.074 | 4 | Mayo Building | Minneapolis | 306 | Fixed Casework - Lab Benches | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1972 | 2019-10-16 | 2 - Good | The millwork is in fair condition overall, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 70 | Per Seat | 515.13 | 1.25 | 1.3 | 1 | 1 | 46876.83 | E201003 | Bleachers | Bleachers | Life Cycle Replacement | Active | Replace Bleachers | Priority 4: Proactive Replacement | 0 | 2026 | 70 | Per Seat | 515.13 | 58596.04 | 0 | 1428.57% | 10000 | 0 | Academic | East
| 301 | 01.074 | 4 | Mayo Building | Minneapolis | 323 | Fixed Casework - Lab Benches | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1972 | 2019-10-16 | 2 - Good | The fixed caework is in fair condition overall, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 5167 | SF Building | 5.22 | 1.25 | 1.3 | 1 | 1 | 35063.26 | C103011 | Millwork General | Millwork General | Life Cycle Replacement | Active | Replace Millwork General | Priority 4: Proactive Replacement | 32 | 2026 | 5167 | SF Building | 5.22 | 43829.08 | 0 | 19.35% | 10000 | 0 | Academic | East
| 304 | 01.074 | 4 | Mayo Building | Minneapolis | 326 | FM200 System - High Density | The fire protection systems include a clean air PyroChem system for the server room. | 2010 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2030 | 2026 | 1 | 4 | Lump Sum | 7700 | 1.25 | 1.3 | 1 | 1 | 40040 | D409099 | Other Fire Protection Systems | Other Fire Protection Systems | Life Cycle Replacement | Active | Replace Other Fire Protection Systems | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Lump Sum | 7700 | 50050 | 0 | 25000% | 10000 | 0 | Academic | East
| 340 | 01.074 | 4 | Mayo Building | Minneapolis | 366 | Fume Hoods | The labs are provided with exhaust fume hoods with ducting. | 1982 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2007 | 2026 | 1 | 7 | Each | 4679.29 | 1.25 | 1.3 | 1 | 1 | 42581.54 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 7 | Each | 4679.29 | 53226.92 | 0 | 14285.71% | 10000 | 0 | Academic | East
| 288 | 01.074 | 4 | Mayo Building | Minneapolis | 310 | Gypsum Board Ceiling - Fire Resistant | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 2019-10-16 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 15 | 1987 | 2026 | 1 | 12153 | SF | 2.65 | 1.25 | 1.3 | 1 | 1 | 41867.09 | C303006 | Painted Ceiling Structures | Painted Ceiling Structures | Life Cycle Replacement | Active | Replace Painted Ceiling Structures | Priority 4: Proactive Replacement | 32 | 2026 | 12153 | SF | 2.65 | 52333.86 | 0 | 8.23% | 10000 | 0 | Academic | East
| 317 | 01.074 | 4 | Mayo Building | Minneapolis | 339 | Gypsum Board Ceiling - Fire Resistant | The building's ceiling finishes include GWB ceiling located in the corridors. | 1982 | 2019-10-16 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 15 | 1997 | 2026 | 1 | 11410 | SF | 2.65 | 1.25 | 1.3 | 1 | 1 | 39307.45 | C303006 | Painted Ceiling Structures | Painted Ceiling Structures | Life Cycle Replacement | Active | Replace Painted Ceiling Structures | Priority 4: Proactive Replacement | 32 | 2026 | 11410 | SF | 2.65 | 49134.31 | 0 | 8.76% | 10000 | 0 | Academic | East
| 302 | 01.074 | 4 | Mayo Building | Minneapolis | 324 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 1972 | 2019-10-16 | 2 - Good | The double doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 4 | Each | 5615.61 | 1.25 | 1.3 | 1 | 1 | 29201.17 | C102024 | Interior - Double Door - Hollow Metal | Interior - Double Door - Hollow Metal | Life Cycle Replacement | Active | Replace Interior - Double Door - Hollow Metal | Priority 4: Proactive Replacement | 32 | 2026 | 4 | Each | 5615.61 | 36501.47 | 0 | 25000% | 10000 | 0 | Academic | East
| 308 | 01.074 | 4 | Mayo Building | Minneapolis | 330 | Interior Windows - Metal | The building includes window units and storefront windows installed in partition openings located on the 300 floor. | 1972 | 2019-10-16 | 2 - Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 75 | 2047 | 2026 | 1 | 646 | SF | 52.22 | 1.25 | 1.3 | 1 | 1 | 43854.36 | C101005 | Interior Windows | Interior Windows | Life Cycle Replacement | Active | Replace Interior Windows | Priority 4: Proactive Replacement | 32 | 2026 | 646 | SF | 52.22 | 54817.95 | 0 | 154.8% | 10000 | 0 | Academic | East
| 292 | 01.074 | 4 | Mayo Building | Minneapolis | 314 | Lighting Fixtures - Exterior | The exterior lighting system consists of surface and recessed mounted fixtures, conduit and wire. | 2000 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | 2035 | 2026 | 1 | 10000 | SF | 2.65 | 1.25 | 1.3 | 1 | 1 | 34450 | D502021 | Interior Lighting (Residential) | Interior Lighting (Residential) | Life Cycle Replacement | Active | Replace Interior Lighting (Residential) | Priority 4: Proactive Replacement | 0 | 2026 | 10000 | SF | 2.65 | 43062.5 | 0 | 10% | 10000 | 0 | Academic | East
| 334 | 01.074 | 4 | Mayo Building | Minneapolis | 359 | Mechanical equipment screens | The building includes corrugated metal mechanical equipment screen with metal frame. | 1972 | 2019-10-16 | 2 - Good | Uniform corrosion was observed on the mechanical equipment screen. Maintenance is recommended to extend the life of the screen which will be covered under the maintenance budget. | 50 | 2022 | 2026 | 1 | 463 | SF | 60.88 | 1.25 | 1.3 | 1 | 1 | 36643.67 | B201005 | Exterior Louvers and Screens | Exterior Louvers and Screens | Life Cycle Replacement | Active | Replace Exterior Louvers and Screens | Priority 4: Proactive Replacement | 45 | 2026 | 463 | SF | 60.88 | 45804.59 | 0 | 215.98% | 10000 | 0 | Academic | East
| 335 | 01.074 | 4 | Mayo Building | Minneapolis | 360 | Motor Control Centres | The electrical distribution system is provided with motor control centres for the supply and control of electrical power to HVAC equipment and other motor loads. | 1972 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 2 | Each | 12166.77 | 1.25 | 1.3 | 1 | 1 | 31633.6 | D501024 | Main Service Panels | Main Service Panels | Life Cycle Replacement | Active | Replace Main Service Panels | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 12166.77 | 39542 | 0 | 50000% | 10000 | 0 | Academic | East
| 321 | 01.074 | 4 | Mayo Building | Minneapolis | 345 | Perimeter Heat - Electric Baseboard | HVAC distribution includes electric baseboard heating in the washrooms and corridors. | 1994 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2012 | 2026 | 1 | 100 | Each | 293.37 | 1.25 | 1.3 | 1 | 1 | 38138.1 | D305010 | Electric Baseboard Heaters | Electric Baseboard Heaters | Life Cycle Replacement | Active | Replace Electric Baseboard Heaters | Priority 4: Proactive Replacement | 0 | 2026 | 100 | Each | 293.37 | 47672.63 | 0 | 1000% | 10000 | 0 | Academic | East
| 289 | 01.074 | 4 | Mayo Building | Minneapolis | 311 | Split DX Unit | Cooling for the fish lab is provided by a Mitsubishi, cooling unit rated 6 tons. | 2008 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2026 | 2026 | 1 | 6 | Each | 3743.74 | 1.25 | 1.3 | 1 | 1 | 29201.17 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 6 | Each | 3743.74 | 36501.47 | 0 | 16666.67% | 10000 | 0 | Academic | East
| 282 | 01.074 | 4 | Mayo Building | Minneapolis | 304 | Transformer - 75 KVA | The building is equipped with three 75 KVA, 600V - 208Y/120V transformers. | 1972 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 3 | Each | 9358.58 | 1.25 | 1.3 | 1 | 1 | 36498.46 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 9358.58 | 45623.08 | 0 | 33333.33% | 10000 | 0 | Academic | East
| 299 | 01.074 | 4 | Mayo Building | Minneapolis | 321 | Transformers - 75 KVA - 1972 | The building is equipped with a 75 KVA, 600V - 208Y/120V transformer on each floor. | 1972 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 3 | Each | 9358.58 | 1.25 | 1.3 | 1 | 1 | 36498.46 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 3 | Each | 9358.58 | 45623.08 | 0 | 33333.33% | 10000 | 0 | Academic | East
| 303 | 01.074 | 4 | Mayo Building | Minneapolis | 325 | Water Heater - Elec - Residential - 85 Gallon | Domestic hot water is provided from a RHEEM, 322 Liter (85 gal), electric, water heater rated at 15000 W. | 2010 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2030 | 2026 | 1 | 4 | Each | 5615.61 | 1.25 | 1.3 | 1 | 1 | 29201.17 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Each | 5615.61 | 36501.47 | 0 | 25000% | 10000 | 0 | Academic | East
| 357 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 388 | Carpet Tile Flooring | The building's floor finishes include carpet floor tiles located in the offices. | 2005 | 2019-11-05 | 2 - Good | The carpet tiles are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 10 | 2015 | 2026 | 1 | 9731 | SF | 7.87 | 1.25 | 1.3 | 1 | 1 | 99557.86 | C302005 | Carpet Floor | Carpet Floor | Life Cycle Replacement | Active | Replace Carpet Floor | Priority 4: Proactive Replacement | 28 | 2026 | 9731 | SF | 7.87 | 124447.33 | 0 | 10.28% | 10000 | 0 | Operations | South
| 388 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 419 | Carpet Tile Flooring | The building's floor finishes include carpet tiles located in the offices. | 2005 | 2019-11-05 | 2 - Good | The carpet tiles are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 10 | 2015 | 2026 | 1 | 8396 | SF | 7.87 | 1.25 | 1.3 | 1 | 1 | 85899.48 | C302005 | Carpet Floor | Carpet Floor | Life Cycle Replacement | Active | Replace Carpet Floor | Priority 4: Proactive Replacement | 28 | 2026 | 8396 | SF | 7.87 | 107374.35 | 0 | 11.91% | 10000 | 0 | Operations | South
| 428 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 461 | Curtain Wall | The building includes a curtain wall system located on the roof. | 1972 | 2019-11-05 | 2 - Good | The curtain wall is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 40 | 2012 | 2026 | 1 | 560 | SF | 108.73 | 1.25 | 1.3 | 1 | 1 | 79155.44 | B202003 | Window Walls | Window Walls | Life Cycle Replacement | Active | Replace Window Walls | Priority 4: Proactive Replacement | 45 | 2026 | 560 | SF | 108.73 | 98944.3 | 0 | 178.57% | 10000 | 0 | Operations | South
| 425 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 458 | Curtain Walls | The building includes a curtain wall system located on the roof. | 1972 | 2019-11-05 | 2 - Good | The curtain walls are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 40 | 2012 | 2026 | 1 | 484 | SF | 108.73 | 1.25 | 1.3 | 1 | 1 | 68412.92 | B202003 | Window Walls | Window Walls | Life Cycle Replacement | Active | Replace Window Walls | Priority 4: Proactive Replacement | 45 | 2026 | 484 | SF | 108.73 | 85516.15 | 0 | 206.61% | 10000 | 0 | Operations | South
| 416 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 449 | DDC/Pneumatic System | HVAC controls include a hybrid DDC/Pneumatic system with basic pc control, moderate sensor types and quantities as well as pneumatic activation of control valves and dampers. | 1994 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2014 | 2026 | 1 | 24111 | SF Building | 2.79 | 1.25 | 1.3 | 1 | 1 | 87450.6 | D306006 | Direct Digital Control Systems | Direct Digital Control Systems | Life Cycle Replacement | Active | Replace Direct Digital Control Systems | Priority 4: Proactive Replacement | 0 | 2026 | 24111 | SF Building | 2.79 | 109313.25 | 0 | 4.15% | 10000 | 0 | Operations | South
| 384 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 415 | DDC/Pneumatic System - Hybrid - Average | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities as well as pneumatic activation of control valves and dampers. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 1992 | 2026 | 1 | 19257 | SF Building | 2.79 | 1.25 | 1.3 | 1 | 1 | 69845.14 | D306006 | Direct Digital Control Systems | Direct Digital Control Systems | Life Cycle Replacement | Active | Replace Direct Digital Control Systems | Priority 4: Proactive Replacement | 0 | 2026 | 19257 | SF Building | 2.79 | 87306.42 | 0 | 5.19% | 10000 | 0 | Operations | South
| 408 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 440 | Distribution Equipment - Motor Control Centres | The electrical distribution system is provided with motor control centres for the supply and control of electrical power to the HVAC equipment and other motor loads. | 1982 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2022 | 2026 | 1 | 4 | Each | 12166.77 | 1.25 | 1.3 | 1 | 1 | 63267.2 | D501024 | Main Service Panels | Main Service Panels | Life Cycle Replacement | Active | Replace Main Service Panels | Priority 4: Proactive Replacement | 0 | 2026 | 4 | Each | 12166.77 | 79084.01 | 0 | 25000% | 10000 | 0 | Operations | South
| 381 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 412 | Domestic Water Distribution - 1972 | The building water distribution system includes a 4&rdquo; for main branch piping, water meter, valves, insulation and fittings. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 13875 | SF Building | 3.65 | 1.25 | 1.3 | 1 | 1 | 65836.88 | D202001 | Domestic Water Piping and Fittings | Domestic Water Piping and Fittings | Life Cycle Replacement | Active | Replace Domestic Water Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 13875 | SF Building | 3.65 | 82296.09 | 0 | 7.21% | 10000 | 0 | Operations | South
| 374 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 405 | DX Computer Unit | Cooling for the Server Room is provided from a Liebert split DX unit having a cooling capacity of approximately 10 tons. | 2008 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2026 | 2026 | 1 | 10 | Each | 3743.74 | 1.25 | 1.3 | 1 | 1 | 48668.62 | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Refrigerant DX Condensing Units - Up to 5 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Up to 5 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 10 | Each | 3743.74 | 60835.78 | 0 | 10000% | 10000 | 0 | Operations | South
| 358 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 389 | Emergency Eyewash Units and Shower Units | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2025 | 2026 | 1 | 5 | Per Lavatory | 7487.48 | 1.25 | 1.3 | 1 | 1 | 48668.62 | D201022 | Universal/Gender Neutral Washroom Fixtures | Universal/Gender Neutral Washroom Fixtures | Life Cycle Replacement | Active | Replace Universal/Gender Neutral Washroom Fixtures | Priority 4: Proactive Replacement | 0 | 2026 | 5 | Per Lavatory | 7487.48 | 60835.78 | 0 | 20000% | 10000 | 0 | Operations | South
| 375 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 406 | Exhaust System - Fume Hoods - 1972 | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 1997 | 2026 | 1 | 16 | Each | 4679.29 | 1.25 | 1.3 | 1 | 1 | 97329.23 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 16 | Each | 4679.29 | 121661.54 | 0 | 6250% | 10000 | 0 | Operations | South
| 376 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 407 | Exhaust System - Fume Hoods - 1997 | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1997 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2022 | 2026 | 1 | 12 | Each | 4679.29 | 1.25 | 1.3 | 1 | 1 | 72996.92 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 12 | Each | 4679.29 | 91246.16 | 0 | 8333.33% | 10000 | 0 | Operations | South
| 379 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 410 | Exterior Hollow Metal Door - Double Leaf | The exterior doors consist of hollow metal double-doors mounted by butt hinges to metal door frames. | 1972 | 2019-11-05 | 2 - Good | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 1 | Each | 58937.34 | 1.25 | 1.3 | 1 | 1 | 76618.54 | B203003 | Exterior - Revolving Doors | Exterior - Revolving Doors | Life Cycle Replacement | Active | Replace Exterior - Revolving Doors | Priority 4: Proactive Replacement | 31 | 2026 | 1 | Each | 58937.34 | 95773.18 | 0 | 100000% | 10000 | 0 | Operations | South
| 412 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 445 | Exterior Hollow Metal Door - Double Leaf | The exterior doors consist of hollow metal double -doors mounted by butt hinges to metal door frames. | 1994 | 2019-11-05 | 2 - Good | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 25 | 2019 | 2026 | 1 | 1 | Each | 58937.34 | 1.25 | 1.3 | 1 | 1 | 76618.54 | B203003 | Exterior - Revolving Doors | Exterior - Revolving Doors | Life Cycle Replacement | Active | Replace Exterior - Revolving Doors | Priority 4: Proactive Replacement | 31 | 2026 | 1 | Each | 58937.34 | 95773.18 | 0 | 100000% | 10000 | 0 | Operations | South
| 418 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 451 | Fire Alarm System - Activation and Notification Devices | This building includes a fire alarm system that includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The field devices in this block are connected to the control panel in Block H as a separate zone. | 1994 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2014 | 2026 | 1 | 12056 | SF Building | 4.58 | 1.25 | 1.3 | 1 | 1 | 71781.42 | D503001 | Fire Alarm Systems | Fire Alarm Systems | Life Cycle Replacement | Active | Replace Fire Alarm Systems | Priority 4: Proactive Replacement | 0 | 2026 | 12056 | SF Building | 4.58 | 89726.78 | 0 | 8.29% | 10000 | 0 | Operations | South
| 419 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 452 | Fire Alarm System - Wiring | This building includes a fire alarm system that includes all conduit, wire, connections to the main control and annunciator panels, pull stations, audio alarm, visual strobes and smoke detectors. | 1994 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2014 | 2026 | 1 | 12056 | SF Building | 4.58 | 1.25 | 1.3 | 1 | 1 | 71781.42 | D503001 | Fire Alarm Systems | Fire Alarm Systems | Life Cycle Replacement | Active | Replace Fire Alarm Systems | Priority 4: Proactive Replacement | 0 | 2026 | 12056 | SF Building | 4.58 | 89726.78 | 0 | 8.29% | 10000 | 0 | Operations | South
| 426 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 459 | Fume Hood Exhaust Fans | The laboratories are equipped with Fume Hood exhaust fans and ducting. | 1998 | 2019-11-05 | 2 - Good | Not significant deficiencies were observed. Replacement can be deferred. | 25 | 2023 | 2026 | 1 | 10 | Each | 4679.29 | 1.25 | 1.3 | 1 | 1 | 60830.77 | E102007 | Fume Hood Systems | Fume Hood Systems | Life Cycle Replacement | Active | Replace Fume Hood Systems | Priority 4: Proactive Replacement | 0 | 2026 | 10 | Each | 4679.29 | 76038.46 | 0 | 10000% | 10000 | 0 | Operations | South
| 366 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 397 | Insulated Metal Panel Roof Cover | The building's atrium is protected with a corrugated insulated metal standing seam roof cover. | 1972 | 2019-11-05 | 2 - Good | The roof cover is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 40 | 2012 | 2026 | 1 | 862 | SF | 24.39 | 1.25 | 1.3 | 1 | 1 | 27331.43 | B301028 | Metal Roofing | Metal Roofing | Life Cycle Replacement | Active | Replace Metal Roofing | Priority 4: Proactive Replacement | 63 | 2026 | 862 | SF | 24.39 | 34164.29 | 1 | 116.01% | 10000 | 0 | Operations | South
| 395 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 426 | Insulated Metal Panel Roof Cover | The atrium is protected with a prefinished insulated metal standing seam roof cover. | 1972 | 2019-11-05 | 2 - Good | The roof cover is in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 40 | 2012 | 2026 | 1 | 691 | SF | 24.39 | 1.25 | 1.3 | 1 | 1 | 21909.54 | B301028 | Metal Roofing | Metal Roofing | Life Cycle Replacement | Active | Replace Metal Roofing | Priority 4: Proactive Replacement | 63 | 2026 | 691 | SF | 24.39 | 82160.76 | 1 | 144.72% | 10000 | 0 | Operations | South
| 431 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 464 | Metal Panels | The building includes corrugated non insulated wall panels located on the roof. | 1982 | 2019-11-05 | 2 - Good | The corrugated metal panels require repainting which will be covered under the maintenance budget. LIfecycle replacement can be deferred. | 40 | 2022 | 2026 | 1 | 1830 | SF | 30.4 | 1.25 | 1.3 | 1 | 1 | 72321.6 | B201028 | Insulated Metal Sandwich Panels | Insulated Metal Sandwich Panels | Life Cycle Replacement | Active | Replace Insulated Metal Sandwich Panels | Priority 4: Proactive Replacement | 41 | 2026 | 1830 | SF | 30.4 | 90402 | 0 | 54.64% | 10000 | 0 | Operations | South
| 424 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 457 | PA System | The building is provided with a Public Announcement (PA) System which includes amplifier, microphone, speakers and shield wire in conduit. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed or reported. Replacement can be deferred. | 15 | 1987 | 2026 | 1 | 35779 | SF Building | 1.86 | 1.25 | 1.3 | 1 | 1 | 86513.62 | D503004 | Public Address and Music Systems | Public Address and Music Systems | Life Cycle Replacement | Active | Replace Public Address and Music Systems | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 1.86 | 108142.03 | 0 | 2.79% | 10000 | 0 | Operations | South
| 380 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 411 | Painted Wall Finish | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2010 | 2019-11-05 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 10 | 2020 | 2026 | 1 | 19267 | SF Building | 3.65 | 1.25 | 1.3 | 1 | 1 | 91421.92 | C301005 | Painted Wall Covering | Painted Wall Covering | Life Cycle Replacement | Active | Replace Painted Wall Covering | Priority 4: Proactive Replacement | 28 | 2026 | 19267 | SF Building | 3.65 | 114277.39 | 0 | 5.19% | 10000 | 0 | Operations | South
| 360 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 391 | Perimeter Heat - Electric Baseboard | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 1990 | 2026 | 1 | 200 | Each | 293.37 | 1.25 | 1.3 | 1 | 1 | 76276.2 | D305010 | Electric Baseboard Heaters | Electric Baseboard Heaters | Life Cycle Replacement | Active | Replace Electric Baseboard Heaters | Priority 4: Proactive Replacement | 0 | 2026 | 200 | Each | 293.37 | 95345.25 | 0 | 500% | 10000 | 0 | Operations | South
| 367 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 398 | Perimeter Heat - Electric Baseboard | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 1990 | 2026 | 1 | 200 | Each | 293.37 | 1.25 | 1.3 | 1 | 1 | 76276.2 | D305010 | Electric Baseboard Heaters | Electric Baseboard Heaters | Life Cycle Replacement | Active | Replace Electric Baseboard Heaters | Priority 4: Proactive Replacement | 0 | 2026 | 200 | Each | 293.37 | 95345.25 | 0 | 500% | 10000 | 0 | Operations | South
| 377 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 408 | Perimeter Heat - Electric Baseboard | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 1990 | 2026 | 1 | 200 | Each | 293.37 | 1.25 | 1.3 | 1 | 1 | 76276.2 | D305010 | Electric Baseboard Heaters | Electric Baseboard Heaters | Life Cycle Replacement | Active | Replace Electric Baseboard Heaters | Priority 4: Proactive Replacement | 0 | 2026 | 200 | Each | 293.37 | 95345.25 | 0 | 500% | 10000 | 0 | Operations | South
| 361 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 392 | Public Address System | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2000 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 15 | 2015 | 2026 | 1 | 35779 | SF Building | 1.86 | 1.25 | 1.3 | 1 | 1 | 86513.62 | D503004 | Public Address and Music Systems | Public Address and Music Systems | Life Cycle Replacement | Active | Replace Public Address and Music Systems | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 1.86 | 108142.03 | 0 | 2.79% | 10000 | 0 | Operations | South
| 382 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 413 | Roof Drainage - Gravity | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 19257 | SF Building | 2.65 | 1.25 | 1.3 | 1 | 1 | 66340.37 | D204001 | Rain Water Drainage Piping and Fittings | Rain Water Drainage Piping and Fittings | Life Cycle Replacement | Active | Replace Rain Water Drainage Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 19257 | SF Building | 2.65 | 82925.46 | 0 | 5.19% | 10000 | 0 | Operations | South
| 365 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 396 | Soffit - Plaster on Metal Lath | C-Blocks bridge soffits are prefinished metal panel soffits. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed, lifecycle replacement can be deferred. | 50 | 2022 | 2026 | 1 | 6781 | SF | 9.59 | 1.25 | 1.3 | 1 | 1 | 84538.73 | B201008 | Exterior Soffits | Exterior Soffits | Life Cycle Replacement | Active | Replace Exterior Soffits | Priority 4: Proactive Replacement | 41 | 2026 | 6781 | SF | 9.59 | 105673.41 | 0 | 14.75% | 10000 | 0 | Operations | South
| 396 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 427 | Terrazzo Flooring - Cast In Place | The building's floor finishes include terrazzo floor finish located in the 200 floor kitchen. | 1972 | 2019-11-05 | 2 - Good | The floor finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 50 | 2022 | 2026 | 1 | 1184 | SF | 39.13 | 1.25 | 1.3 | 1 | 1 | 60228.9 | C302002 | Terrazzo Floor | Terrazzo Floor | Life Cycle Replacement | Active | Replace Terrazzo Floor | Priority 4: Proactive Replacement | 28 | 2026 | 1184 | SF | 39.13 | 75286.12 | 0 | 84.46% | 10000 | 0 | Operations | South
| 368 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 399 | Transformer - 75 KVA | The building is equipped with two 75 kVA, 600V - 208Y/120V, 3-Phase, transformers on each floor. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 7 | Each | 9358.58 | 1.25 | 1.3 | 1 | 1 | 85163.08 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 7 | Each | 9358.58 | 106453.85 | 0 | 14285.71% | 10000 | 0 | Operations | South
| 409 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 441 | Transformers - 75 KVA | The electrical system is equipped with 75 KVA, 600V - 208Y/120V transformers on each floor. | 1982 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2032 | 2026 | 1 | 7 | Each | 9358.58 | 1.25 | 1.3 | 1 | 1 | 85163.08 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 7 | Each | 9358.58 | 106453.85 | 0 | 14285.71% | 10000 | 0 | Operations | South
| 430 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 463 | Vinyl sheet | The building's floor finishes include sheet vinyl flooring located in D205 computer lab | 2009 | 2019-11-05 | 2 - Good | No deficiencies were observed or reported, lifecycle replacement can be deferred. | 50 | 2059 | 2026 | 1 | 1216 | SF | 51.36 | 1.25 | 1.3 | 1 | 1 | 81189.89 | C302006 | Masonry and Stone Floor | Masonry and Stone Floor | Life Cycle Replacement | Active | Replace Masonry and Stone Floor | Priority 4: Proactive Replacement | 28 | 2026 | 1216 | SF | 51.36 | 101487.36 | 0 | 82.24% | 10000 | 0 | Operations | South
| 359 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 390 | Water Heater - Elec - 43 Litre | The domestic hot water is provided by a SpaceSaver, 43-Litre, electric, water heater rated at 3.0 KW. | 2010 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2030 | 2026 | 1 | 1 | Each | 5615.61 | 1.25 | 1.3 | 1 | 1 | 7300.29 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 5615.61 | 9125.37 | 0 | 100000% | 10000 | 0 | Operations | South
| 405 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 437 | Water Heaters | The domestic hot water is provided by three 454 Liters (120-gal), Rheem, electric, water heaters, each rated at 30000 W. | 2010 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2030 | 2026 | 1 | 12 | Each | 5615.61 | 1.25 | 1.3 | 1 | 1 | 87603.52 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 12 | Each | 5615.61 | 109504.4 | 0 | 8333.33% | 10000 | 0 | Operations | South
| 385 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 416 | Wet Standpipe System | The fire protection systems consists of a wet fire standpipe system with backflow protection that Includes distribution piping and shutoff valves. | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 19257 | SF Building | 2.43 | 1.25 | 1.3 | 1 | 1 | 60832.86 | D402001 | Standpipes | Standpipes | Life Cycle Replacement | Active | Replace Standpipes | Priority 4: Proactive Replacement | 0 | 2026 | 19257 | SF Building | 2.43 | 76041.08 | 0 | 5.19% | 10000 | 0 | Operations | South
| 389 | 01.053 | 5 | Northrop Auditorium | Saint Paul | 420 | Wet Standpipe System | The fire protection systems include a wet fire standpipe system with backflow protection including distribution piping and shutoff valves | 1972 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 27857 | SF Building | 2.43 | 1.25 | 1.3 | 1 | 1 | 88000.26 | D402001 | Standpipes | Standpipes | Life Cycle Replacement | Active | Replace Standpipes | Priority 4: Proactive Replacement | 0 | 2026 | 27857 | SF Building | 2.43 | 110000.33 | 0 | 3.59% | 10000 | 0 | Operations | South
| 442 | 31.896 | 6 | Nova Far Detector Building | Orr | 477 | Acoustic Tile Ceiling - Exposed T-bar | The predominant ceiling finish in the building is suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids. | 1998 | 2019-11-04 | 2 - Good | The ceiling tiles are in good condition overall, no deficiencies were observed or reported. Lifecycle replacement can be deferred. | 30 | 2028 | 2026 | 1 | 13993 | SF | 6.15 | 1.25 | 1.3 | 1.18 | 1 | 132011.36 | C303004 | Adhered Acoustic Tile Ceiling | Adhered Acoustic Tile Ceiling | Life Cycle Replacement | Active | Replace Adhered Acoustic Tile Ceiling | Priority 4: Proactive Replacement | 32 | 2026 | 13993 | SF | 6.15 | 165014.2 | 0 | 7.15% | 10000 | 0 | Academic | East
| 462 | 31.896 | 6 | Nova Far Detector Building | Orr | 497 | DDC/Pneumatic System - Hybrid | HVAC controls include a Hybrid DDC /Pneumatic system for system optimization, basic pc control, moderate sensor types with pneumatic activation of control valves and dampers. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 1992 | 2026 | 1 | 31850 | SF Building | 2.79 | 1.25 | 1.3 | 1.18 | 1 | 136313.54 | D306006 | Direct Digital Control Systems | Direct Digital Control Systems | Life Cycle Replacement | Active | Replace Direct Digital Control Systems | Priority 4: Proactive Replacement | 0 | 2026 | 31850 | SF Building | 2.79 | 170391.93 | 0 | 3.14% | 10000 | 0 | Academic | East
| 475 | 31.896 | 6 | Nova Far Detector Building | Orr | 510 | DDC/Pneumatic System - Hybrid - Average | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities including pneumatic activation of control valves and dampers. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 1992 | 2026 | 1 | 27857 | SF Building | 2.79 | 1.25 | 1.3 | 1.18 | 1 | 119224.06 | D306006 | Direct Digital Control Systems | Direct Digital Control Systems | Life Cycle Replacement | Active | Replace Direct Digital Control Systems | Priority 4: Proactive Replacement | 0 | 2026 | 27857 | SF Building | 2.79 | 149030.08 | 0 | 3.59% | 10000 | 0 | Academic | East
| 493 | 31.896 | 6 | Nova Far Detector Building | Orr | 530 | Distribution Switchboards | The electrical system is provided with distribution switchboards which include incoming feeders, distribution breakers and distribution feeders. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 97329.54 | 1.25 | 1.3 | 1.18 | 1 | 149303.51 | D501022 | Main Service Switchboards - 800A to 1600A | Main Service Switchboards - 800A to 1600A | Life Cycle Replacement | Active | Replace Main Service Switchboards - 800A to 1600A | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 97329.54 | 186629.39 | 0 | 100000% | 10000 | 0 | Academic | East
| 481 | 31.896 | 6 | Nova Far Detector Building | Orr | 516 | Distribution Switchboards, Panelboards and Feeders | The electrical distribution system includes essential and normal power switchboards, panelboards, feeders, transformers, vertical bus duct, wire, conduit and associated equipment. | 1982 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2022 | 2026 | 1 | 1 | Each | 97329.54 | 1.25 | 1.3 | 1.18 | 1 | 149303.51 | D501022 | Main Service Switchboards - 800A to 1600A | Main Service Switchboards - 800A to 1600A | Life Cycle Replacement | Active | Replace Main Service Switchboards - 800A to 1600A | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 97329.54 | 186629.39 | 0 | 100000% | 10000 | 0 | Academic | East
| 463 | 31.896 | 6 | Nova Far Detector Building | Orr | 498 | Distribution Switchboards, Panelboards and Feeders - 1972 | The electrical distribution system for the 1972 section includes essential and normal switchboards, panelboards, feeders, vertical bus duct, wire, conduit and associated equipment. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 97329.54 | 1.25 | 1.3 | 1.18 | 1 | 149303.51 | D501022 | Main Service Switchboards - 800A to 1600A | Main Service Switchboards - 800A to 1600A | Life Cycle Replacement | Active | Replace Main Service Switchboards - 800A to 1600A | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 97329.54 | 186629.39 | 0 | 100000% | 10000 | 0 | Academic | East
| 473 | 31.896 | 6 | Nova Far Detector Building | Orr | 508 | Domestic Water Distribution - 1972 | The building water distribution system includes a 4&rdquo; for main branch piping, water meter, valves, insulation and fittings. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 25704 | SF Building | 3.65 | 1.25 | 1.3 | 1.18 | 1 | 143919.27 | D202001 | Domestic Water Piping and Fittings | Domestic Water Piping and Fittings | Life Cycle Replacement | Active | Replace Domestic Water Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 25704 | SF Building | 3.65 | 179899.08 | 0 | 3.89% | 10000 | 0 | Academic | East
| 452 | 31.896 | 6 | Nova Far Detector Building | Orr | 487 | Eggcrate Ceiling - Exposed T-bar | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 2019-11-04 | 2 - Good | The ceiling finish is in fair condition overall, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 11044 | SF | 7.87 | 1.25 | 1.3 | 1.18 | 1 | 133329.57 | C303007 | Suspended Acoustic Ceiling Panels | Suspended Acoustic Ceiling Panels | Life Cycle Replacement | Active | Replace Suspended Acoustic Ceiling Panels | Priority 4: Proactive Replacement | 32 | 2026 | 11044 | SF | 7.87 | 166661.97 | 0 | 9.05% | 10000 | 0 | Academic | East
| 458 | 31.896 | 6 | Nova Far Detector Building | Orr | 493 | Eggcrate Ceiling - Exposed T-bar | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 2019-11-04 | 2 - Good | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 11840 | SF | 7.87 | 1.25 | 1.3 | 1.18 | 1 | 142939.35 | C303007 | Suspended Acoustic Ceiling Panels | Suspended Acoustic Ceiling Panels | Life Cycle Replacement | Active | Replace Suspended Acoustic Ceiling Panels | Priority 4: Proactive Replacement | 32 | 2026 | 11840 | SF | 7.87 | 178674.18 | 0 | 8.45% | 10000 | 0 | Academic | East
| 472 | 31.896 | 6 | Nova Far Detector Building | Orr | 507 | Eggcrate Ceiling - Exposed T-bar | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 2019-11-04 | 2 - Good | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 11421 | SF | 7.87 | 1.25 | 1.3 | 1.18 | 1 | 137880.94 | C303007 | Suspended Acoustic Ceiling Panels | Suspended Acoustic Ceiling Panels | Life Cycle Replacement | Active | Replace Suspended Acoustic Ceiling Panels | Priority 4: Proactive Replacement | 32 | 2026 | 11421 | SF | 7.87 | 172351.17 | 0 | 8.76% | 10000 | 0 | Academic | East
| 468 | 31.896 | 6 | Nova Far Detector Building | Orr | 503 | Emergency Eyewash Units and Shower Units | Plumbing fixtures include emergency eyewash and showers stations installed throughout the building. | 2000 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2025 | 2026 | 1 | 12 | Per Lavatory | 7487.48 | 1.25 | 1.3 | 1.18 | 1 | 137829.53 | D201022 | Universal/Gender Neutral Washroom Fixtures | Universal/Gender Neutral Washroom Fixtures | Life Cycle Replacement | Active | Replace Universal/Gender Neutral Washroom Fixtures | Priority 4: Proactive Replacement | 0 | 2026 | 12 | Per Lavatory | 7487.48 | 172286.91 | 0 | 8333.33% | 10000 | 0 | Academic | East
| 446 | 31.896 | 6 | Nova Far Detector Building | Orr | 481 | Epoxy Flooring | The building's floor finishes include cement epoxy floor finish located located in the laboratories on the 400 floor level. | 2000 | 2019-11-04 | 2 - Good | The epoxy floor finish is in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 15 | 2015 | 2026 | 1 | 23142 | SF | 3.65 | 1.25 | 1.3 | 1.18 | 1 | 129574.37 | C302007 | Painted / Sealed Floor | Painted / Sealed Floor | Life Cycle Replacement | Active | Replace Painted / Sealed Floor | Priority 4: Proactive Replacement | 32 | 2026 | 23142 | SF | 3.65 | 161967.97 | 0 | 4.32% | 10000 | 0 | Academic | East
| 447 | 31.896 | 6 | Nova Far Detector Building | Orr | 482 | Gypsum Board Ceiling - Fire Resistant | The building's ceiling finishes include GWB ceiling located in the corridors. | 1972 | 2019-11-04 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 15 | 1987 | 2026 | 1 | 37017 | SF | 2.65 | 1.25 | 1.3 | 1.18 | 1 | 150477.81 | C303006 | Painted Ceiling Structures | Painted Ceiling Structures | Life Cycle Replacement | Active | Replace Painted Ceiling Structures | Priority 4: Proactive Replacement | 32 | 2026 | 37017 | SF | 2.65 | 188097.26 | 0 | 2.7% | 10000 | 0 | Academic | East
| 459 | 31.896 | 6 | Nova Far Detector Building | Orr | 494 | Gypsum Board Ceiling - Fire Resistant | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 2019-11-04 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 15 | 1987 | 2026 | 1 | 39827 | SF | 2.65 | 1.25 | 1.3 | 1.18 | 1 | 161900.74 | C303006 | Painted Ceiling Structures | Painted Ceiling Structures | Life Cycle Replacement | Active | Replace Painted Ceiling Structures | Priority 4: Proactive Replacement | 32 | 2026 | 39827 | SF | 2.65 | 202375.92 | 0 | 2.51% | 10000 | 0 | Academic | East
| 467 | 31.896 | 6 | Nova Far Detector Building | Orr | 502 | Hollow Metal Single Doors | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 37 | Each | 2527.14 | 1.25 | 1.3 | 1.18 | 1 | 143435.41 | C102022 | Interior - Single Door - Wood | Interior - Single Door - Wood | Life Cycle Replacement | Active | Replace Interior - Single Door - Wood | Priority 4: Proactive Replacement | 32 | 2026 | 37 | Each | 2527.14 | 179294.27 | 0 | 2702.7% | 10000 | 0 | Academic | East
| 457 | 31.896 | 6 | Nova Far Detector Building | Orr | 492 | Interior Hollow Metal Swing Doors - Double Leaf | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 1972 | 2019-11-04 | 2 - Good | The doors are functioning as intended, lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 14 | Each | 5615.61 | 1.25 | 1.3 | 1.18 | 1 | 120600.84 | C102024 | Interior - Double Door - Hollow Metal | Interior - Double Door - Hollow Metal | Life Cycle Replacement | Active | Replace Interior - Double Door - Hollow Metal | Priority 4: Proactive Replacement | 32 | 2026 | 14 | Each | 5615.61 | 150751.05 | 0 | 7142.86% | 10000 | 0 | Academic | East
| 445 | 31.896 | 6 | Nova Far Detector Building | Orr | 480 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | The interior doors include hollow metal double doors with vision panels. | 1972 | 2019-11-04 | 2 - Good | The double doors are in good condition overall, and are functioning as intended. Lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 13 | Each | 5615.61 | 1.25 | 1.3 | 1.18 | 1 | 111986.49 | C102024 | Interior - Double Door - Hollow Metal | Interior - Double Door - Hollow Metal | Life Cycle Replacement | Active | Replace Interior - Double Door - Hollow Metal | Priority 4: Proactive Replacement | 32 | 2026 | 13 | Each | 5615.61 | 139983.12 | 0 | 7692.31% | 10000 | 0 | Academic | East
| 456 | 31.896 | 6 | Nova Far Detector Building | Orr | 491 | Interior Windows - Metal | The building includes window units and storefront windows installed in partition openings located on the 200 floor level. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 75 | 2047 | 2026 | 1 | 1884 | SF | 52.22 | 1.25 | 1.3 | 1.18 | 1 | 150918.72 | C101005 | Interior Windows | Interior Windows | Life Cycle Replacement | Active | Replace Interior Windows | Priority 4: Proactive Replacement | 32 | 2026 | 1884 | SF | 52.22 | 188648.41 | 0 | 53.08% | 10000 | 0 | Academic | East
| 494 | 31.896 | 6 | Nova Far Detector Building | Orr | 531 | Main Distribution Switchboard | The electrical system is provided with a 1000A, 600Y/347V, 3-Phase, 4-Wire, Main Breaker Distribution Switchboard which includes incoming feeder, main breaker, distribution breakers and distribution feeders. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 97329.54 | 1.25 | 1.3 | 1.18 | 1 | 149303.51 | D501022 | Main Service Switchboards - 800A to 1600A | Main Service Switchboards - 800A to 1600A | Life Cycle Replacement | Active | Replace Main Service Switchboards - 800A to 1600A | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 97329.54 | 186629.39 | 0 | 100000% | 10000 | 0 | Academic | East
| 495 | 31.896 | 6 | Nova Far Detector Building | Orr | 532 | Main Distribution Switchboard | The electrical system for the building is provided with a 3000A, 600V, 3-Phase, 4-Wire, Main Breaker Switchboard which includes incoming feeder, main breaker, distribution feeders and distribution feeders. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 97329.54 | 1.25 | 1.3 | 1.18 | 1 | 149303.51 | D501022 | Main Service Switchboards - 800A to 1600A | Main Service Switchboards - 800A to 1600A | Life Cycle Replacement | Active | Replace Main Service Switchboards - 800A to 1600A | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 97329.54 | 186629.39 | 0 | 100000% | 10000 | 0 | Academic | East
| 441 | 31.896 | 6 | Nova Far Detector Building | Orr | 476 | Painted Wall Finish | Standard paint finish is applied to the GWB and CMU walls. | 2012 | 2019-11-04 | 2 - Good | The painted wall finish is in good condition overall, no major deficiencies were observed. Lifecycle replacement can be deferred. | 10 | 2022 | 2026 | 1 | 25855 | SF Building | 3.65 | 1.25 | 1.3 | 1.18 | 1 | 144764.73 | C301005 | Painted Wall Covering | Painted Wall Covering | Life Cycle Replacement | Active | Replace Painted Wall Covering | Priority 4: Proactive Replacement | 32 | 2026 | 25855 | SF Building | 3.65 | 180955.91 | 0 | 3.87% | 10000 | 0 | Academic | East
| 471 | 31.896 | 6 | Nova Far Detector Building | Orr | 506 | Painted Wall Finish | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2005 | 2019-11-04 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 10 | 2015 | 2026 | 1 | 27857 | SF Building | 3.65 | 1.25 | 1.3 | 1.18 | 1 | 155974.13 | C301005 | Painted Wall Covering | Painted Wall Covering | Life Cycle Replacement | Active | Replace Painted Wall Covering | Priority 4: Proactive Replacement | 32 | 2026 | 27857 | SF Building | 3.65 | 194967.66 | 0 | 3.59% | 10000 | 0 | Academic | East
| 455 | 31.896 | 6 | Nova Far Detector Building | Orr | 490 | Public Address System | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2000 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 15 | 2015 | 2026 | 1 | 46220 | SF Building | 1.86 | 1.25 | 1.3 | 1.18 | 1 | 131876.75 | D503004 | Public Address and Music Systems | Public Address and Music Systems | Life Cycle Replacement | Active | Replace Public Address and Music Systems | Priority 4: Proactive Replacement | 0 | 2026 | 46220 | SF Building | 1.86 | 164845.94 | 0 | 2.16% | 10000 | 0 | Academic | East
| 474 | 31.896 | 6 | Nova Far Detector Building | Orr | 509 | Roof Drainage - Gravity | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 27857 | SF Building | 2.65 | 1.25 | 1.3 | 1.18 | 1 | 113241.49 | D204001 | Rain Water Drainage Piping and Fittings | Rain Water Drainage Piping and Fittings | Life Cycle Replacement | Active | Replace Rain Water Drainage Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 27857 | SF Building | 2.65 | 141551.86 | 0 | 3.59% | 10000 | 0 | Academic | East
| 469 | 31.896 | 6 | Nova Far Detector Building | Orr | 504 | Sanitary Waste - Gravity Discharge | The building is provided with a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 19257 | SF Building | 4.15 | 1.25 | 1.3 | 1.18 | 1 | 122591.99 | D203001 | Sanitary Waste and Vent Piping and Fittings | Sanitary Waste and Vent Piping and Fittings | Life Cycle Replacement | Active | Replace Sanitary Waste and Vent Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 19257 | SF Building | 4.15 | 153239.98 | 0 | 5.19% | 10000 | 0 | Academic | East
| 449 | 31.896 | 6 | Nova Far Detector Building | Orr | 484 | Wet Standpipe System | The fire protection systems include a wet standpipe system with distribution piping and shutoff valves. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 35779 | SF Building | 2.43 | 1.25 | 1.3 | 1.18 | 1 | 133370.52 | D402001 | Standpipes | Standpipes | Life Cycle Replacement | Active | Replace Standpipes | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 2.43 | 166713.14 | 0 | 2.79% | 10000 | 0 | Academic | East
| 479 | 31.896 | 6 | Nova Far Detector Building | Orr | 514 | Wet Standpipe System | The fire protection systems include a wet fire standpipe system with distribution piping and shutoff valves. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 37954 | SF Building | 2.43 | 1.25 | 1.3 | 1.18 | 1 | 141478.09 | D402001 | Standpipes | Standpipes | Life Cycle Replacement | Active | Replace Standpipes | Priority 4: Proactive Replacement | 0 | 2026 | 37954 | SF Building | 2.43 | 176847.61 | 0 | 2.63% | 10000 | 0 | Academic | East
| 513 | 04.750 | 7 | Science | Mankato | 551 | Carpet Tile Flooring | The building's floor finishes include carpet tiles located in the offices. | 2005 | 2019-11-07 | 2 - Good | The carpet tiles are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 10 | 2015 | 2026 | 1 | 16146 | SF | 7.87 | 1.25 | 1.3 | 1.25 | 1 | 206487.16 | C302005 | Carpet Floor | Carpet Floor | Life Cycle Replacement | Active | Replace Carpet Floor | Priority 4: Proactive Replacement | 40 | 2026 | 16146 | SF | 7.87 | 258108.95 | 0 | 6.19% | 10000 | 0 | Academic | South
| 502 | 04.750 | 7 | Science | Mankato | 540 | Central AHU - 10000 CFM | The HVAC system has a central Air Handling Unit with cooling coils and electric heating coils rated 10000 CFM. | 1990 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2020 | 2026 | 1 | 1 | Each | 127120.84 | 1.25 | 1.3 | 1.25 | 1 | 206571.37 | D304041 | Air Handling Units - Modular - Up to 20,000 CFM | Air Handling Units - Modular - Up to 20,000 CFM | Life Cycle Replacement | Active | Replace Air Handling Units - Modular - Up to 20,000 CFM | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 127120.84 | 258214.21 | 0 | 100000% | 10000 | 0 | Academic | South
| 503 | 04.750 | 7 | Science | Mankato | 541 | Central AHU - 2000 CFM | The HVAC system includes a central Air Handling Unit with cooling coils and electric heating coils rated 2000 CFM. | 1984 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2014 | 2026 | 1 | 1 | Each | 127120.84 | 1.25 | 1.3 | 1.25 | 1 | 206571.37 | D304041 | Air Handling Units - Modular - Up to 20,000 CFM | Air Handling Units - Modular - Up to 20,000 CFM | Life Cycle Replacement | Active | Replace Air Handling Units - Modular - Up to 20,000 CFM | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 127120.84 | 258214.21 | 0 | 100000% | 10000 | 0 | Academic | South
| 504 | 04.750 | 7 | Science | Mankato | 542 | DDC/Pneumatic System | HVAC controls include a hybrid DDC/Pneumatic system with basic pc control, moderate sensor types and quantities, as well as pneumatic activation of control valves and dampers. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 1992 | 2026 | 1 | 35779 | SF Building | 2.79 | 1.25 | 1.3 | 1.25 | 1 | 162213.04 | D306006 | Direct Digital Control Systems | Direct Digital Control Systems | Life Cycle Replacement | Active | Replace Direct Digital Control Systems | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 2.79 | 202766.3 | 0 | 2.79% | 10000 | 0 | Academic | South
| 510 | 04.750 | 7 | Science | Mankato | 548 | DDC/Pneumatic System - Hybrid | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities; and includes pneumatic activation of control valves and dampers. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 1992 | 2026 | 1 | 46220 | SF Building | 2.79 | 1.25 | 1.3 | 1.25 | 1 | 209549.93 | D306006 | Direct Digital Control Systems | Direct Digital Control Systems | Life Cycle Replacement | Active | Replace Direct Digital Control Systems | Priority 4: Proactive Replacement | 0 | 2026 | 46220 | SF Building | 2.79 | 261937.41 | 0 | 2.16% | 10000 | 0 | Academic | South
| 532 | 04.750 | 7 | Science | Mankato | 570 | DDC/Pneumatic System - Hybrid | HVAC controls consists of a hybrid DDC/Pneumatic system which includes basic pc control, moderate sensor types and quantities, pneumatic activation of control valves and dampers. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 1992 | 2026 | 1 | 37954 | SF Building | 2.79 | 1.25 | 1.3 | 1.25 | 1 | 172073.95 | D306006 | Direct Digital Control Systems | Direct Digital Control Systems | Life Cycle Replacement | Active | Replace Direct Digital Control Systems | Priority 4: Proactive Replacement | 0 | 2026 | 37954 | SF Building | 2.79 | 215092.43 | 0 | 2.63% | 10000 | 0 | Academic | South
| 521 | 04.750 | 7 | Science | Mankato | 559 | Distribution Equipment - Motor Control Centres | The electrical distribution system for the building includes a motor control centre for the supply and control of electrical power to HVAC equipment and other motor loads and air handing units and includes wire and conduit. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 97329.54 | 1.25 | 1.3 | 1.25 | 1 | 158160.5 | D501022 | Main Service Switchboards - 800A to 1600A | Main Service Switchboards - 800A to 1600A | Life Cycle Replacement | Active | Replace Main Service Switchboards - 800A to 1600A | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 97329.54 | 197700.63 | 0 | 100000% | 10000 | 0 | Academic | South
| 522 | 04.750 | 7 | Science | Mankato | 560 | Distribution Switchboards, Panelboards and Feeders | The electrical distribution system for the building includes essential and normal power switchboards, panelboards, feeders, vertical bus duct, wire, conduit and associated equipment. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 97329.54 | 1.25 | 1.3 | 1.25 | 1 | 158160.5 | D501022 | Main Service Switchboards - 800A to 1600A | Main Service Switchboards - 800A to 1600A | Life Cycle Replacement | Active | Replace Main Service Switchboards - 800A to 1600A | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 97329.54 | 197700.63 | 0 | 100000% | 10000 | 0 | Academic | South
| 535 | 04.750 | 7 | Science | Mankato | 573 | Emergency Eyewash and Shower Units | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2025 | 2026 | 1 | 15 | Per Lavatory | 7487.48 | 1.25 | 1.3 | 1.25 | 1 | 182507.33 | D201022 | Universal/Gender Neutral Washroom Fixtures | Universal/Gender Neutral Washroom Fixtures | Life Cycle Replacement | Active | Replace Universal/Gender Neutral Washroom Fixtures | Priority 4: Proactive Replacement | 0 | 2026 | 15 | Per Lavatory | 7487.48 | 228134.16 | 0 | 6666.67% | 10000 | 0 | Academic | South
| 534 | 04.750 | 7 | Science | Mankato | 572 | Hydraulic Passenger Elevator - 2-Storey | The conveying equipment includes a 2 storey hydraulic passenger elevator with a capacity of 4000LB (1814Kg). | 1982 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2012 | 2026 | 1 | 1 | Each | 133965.37 | 1.25 | 1.3 | 1.25 | 1 | 217693.73 | D101003 | Freight Elevators - Up to 3 Storey | Freight Elevators - Up to 3 Storey | Life Cycle Replacement | Active | Replace Freight Elevators - Up to 3 Storey | Priority 4: Proactive Replacement | 53 | 2026 | 1 | Each | 133965.37 | 272117.16 | 0 | 100000% | 10000 | 0 | Academic | South
| 507 | 04.750 | 7 | Science | Mankato | 545 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 1972 | 2019-11-07 | 2 - Good | The doors are functioning as intended, lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 23 | Each | 5615.61 | 1.25 | 1.3 | 1.25 | 1 | 209883.42 | C102024 | Interior - Double Door - Hollow Metal | Interior - Double Door - Hollow Metal | Life Cycle Replacement | Active | Replace Interior - Double Door - Hollow Metal | Priority 4: Proactive Replacement | 40 | 2026 | 23 | Each | 5615.61 | 262354.28 | 0 | 4347.83% | 10000 | 0 | Academic | South
| 527 | 04.750 | 7 | Science | Mankato | 565 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | The interior doors include hollow metal double doors with vision panels. | 1972 | 2019-11-07 | 2 - Good | The double doors are in fair condition overall, and are functioning as intended. Lifecycle replacement can be deferred. | 30 | 2002 | 2026 | 1 | 21 | Each | 5615.61 | 1.25 | 1.3 | 1.25 | 1 | 191632.69 | C102024 | Interior - Double Door - Hollow Metal | Interior - Double Door - Hollow Metal | Life Cycle Replacement | Active | Replace Interior - Double Door - Hollow Metal | Priority 4: Proactive Replacement | 40 | 2026 | 21 | Each | 5615.61 | 239540.86 | 0 | 4761.9% | 10000 | 0 | Academic | South
| 536 | 04.750 | 7 | Science | Mankato | 574 | Laboratory Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 1990 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 35 | 2025 | 2026 | 1 | 150 | Each | 977.9 | 1.25 | 1.3 | 1.25 | 1 | 238363.13 | D201004 | Sinks | Sinks | Life Cycle Replacement | Active | Replace Sinks | Priority 4: Proactive Replacement | 0 | 2026 | 150 | Each | 977.9 | 297953.91 | 0 | 666.67% | 10000 | 0 | Academic | South
| 498 | 04.750 | 7 | Science | Mankato | 536 | Painted Wall Finish | Standard paint finish is applied to the GWB, and Concrete Masonry walls. | 2010 | 2019-11-07 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 10 | 2020 | 2026 | 1 | 37017 | SF Building | 3.65 | 1.25 | 1.3 | 1.25 | 1 | 219557.08 | C301005 | Painted Wall Covering | Painted Wall Covering | Life Cycle Replacement | Active | Replace Painted Wall Covering | Priority 4: Proactive Replacement | 40 | 2026 | 37017 | SF Building | 3.65 | 274446.35 | 0 | 2.7% | 10000 | 0 | Academic | South
| 528 | 04.750 | 7 | Science | Mankato | 566 | Painted Wall Finish | Standard paint finish is applied to the GWB, and Concrete Masonry walls. | 2010 | 2019-11-07 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 10 | 2020 | 2026 | 1 | 37964 | SF Building | 3.65 | 1.25 | 1.3 | 1.25 | 1 | 225173.98 | C301005 | Painted Wall Covering | Painted Wall Covering | Life Cycle Replacement | Active | Replace Painted Wall Covering | Priority 4: Proactive Replacement | 40 | 2026 | 37964 | SF Building | 3.65 | 281467.47 | 0 | 2.63% | 10000 | 0 | Academic | South
| 520 | 04.750 | 7 | Science | Mankato | 558 | Perimeter Heat - Electric Baseboard | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 1990 | 2026 | 1 | 400 | Each | 293.37 | 1.25 | 1.3 | 1.25 | 1 | 190690.5 | D305010 | Electric Baseboard Heaters | Electric Baseboard Heaters | Life Cycle Replacement | Active | Replace Electric Baseboard Heaters | Priority 4: Proactive Replacement | 0 | 2026 | 400 | Each | 293.37 | 238363.13 | 0 | 250% | 10000 | 0 | Academic | South
| 531 | 04.750 | 7 | Science | Mankato | 569 | Perimeter Heat - Electric Baseboard | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 1990 | 2026 | 1 | 400 | Each | 293.37 | 1.25 | 1.3 | 1.25 | 1 | 190690.5 | D305010 | Electric Baseboard Heaters | Electric Baseboard Heaters | Life Cycle Replacement | Active | Replace Electric Baseboard Heaters | Priority 4: Proactive Replacement | 0 | 2026 | 400 | Each | 293.37 | 238363.13 | 0 | 250% | 10000 | 0 | Academic | South
| 538 | 04.750 | 7 | Science | Mankato | 576 | Public Address System | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2000 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 15 | 2015 | 2026 | 1 | 68781 | SF Building | 1.86 | 1.25 | 1.3 | 1.25 | 1 | 207890.57 | D503004 | Public Address and Music Systems | Public Address and Music Systems | Life Cycle Replacement | Active | Replace Public Address and Music Systems | Priority 4: Proactive Replacement | 0 | 2026 | 68781 | SF Building | 1.86 | 259863.22 | 0 | 1.45% | 10000 | 0 | Academic | South
| 501 | 04.750 | 7 | Science | Mankato | 539 | Roof Drainage - Gravity | Rain water drainage consists of roof drains, interior piping and discharge by gravity flow to the municipal main. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 35779 | SF Building | 2.65 | 1.25 | 1.3 | 1.25 | 1 | 154073.32 | D204001 | Rain Water Drainage Piping and Fittings | Rain Water Drainage Piping and Fittings | Life Cycle Replacement | Active | Replace Rain Water Drainage Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 2.65 | 192591.65 | 0 | 2.79% | 10000 | 0 | Academic | South
| 509 | 04.750 | 7 | Science | Mankato | 547 | Roof Drainage - Gravity | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 46220 | SF Building | 2.65 | 1.25 | 1.3 | 1.25 | 1 | 199034.88 | D204001 | Rain Water Drainage Piping and Fittings | Rain Water Drainage Piping and Fittings | Life Cycle Replacement | Active | Replace Rain Water Drainage Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 46220 | SF Building | 2.65 | 248793.59 | 0 | 2.16% | 10000 | 0 | Academic | South
| 530 | 04.750 | 7 | Science | Mankato | 568 | Roof Drainage - Gravity | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 37594 | SF Building | 2.65 | 1.25 | 1.3 | 1.25 | 1 | 161889.16 | D204001 | Rain Water Drainage Piping and Fittings | Rain Water Drainage Piping and Fittings | Life Cycle Replacement | Active | Replace Rain Water Drainage Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 37594 | SF Building | 2.65 | 202361.45 | 0 | 2.66% | 10000 | 0 | Academic | South
| 524 | 04.750 | 7 | Science | Mankato | 562 | Sanitary Waste - Gravity Discharge | The building includes an extensive sanitary waste system of cast iron, copper and PVC piping with gravity discharge to the municipal system. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 27857 | SF Building | 4.15 | 1.25 | 1.3 | 1.25 | 1 | 187860.64 | D203001 | Sanitary Waste and Vent Piping and Fittings | Sanitary Waste and Vent Piping and Fittings | Life Cycle Replacement | Active | Replace Sanitary Waste and Vent Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 27857 | SF Building | 4.15 | 234825.8 | 0 | 3.59% | 10000 | 0 | Academic | South
| 519 | 04.750 | 7 | Science | Mankato | 557 | Single-Ply Membrane Roof Cover - Ballasted | The roof is protected with a single-ply ballasted EPDM membrane and rigid insulation board substrate. | 2000 | 2019-11-07 | 2 - Good | The roof is in fair condition overall, lifecycle replacement can be deferred. | 20 | 2020 | 2026 | 1 | 3454 | SF | 16.1 | 1.25 | 1.3 | 1.25 | 1 | 90365.28 | B301023 | Conventional - Single Ply Membrane | Conventional - Single Ply Membrane | Life Cycle Replacement | Active | Replace Conventional - Single Ply Membrane | Priority 4: Proactive Replacement | 75 | 2026 | 3454 | SF | 16.1 | 112956.59 | 0 | 28.95% | 10000 | 0 | Academic | South
| 537 | 04.750 | 7 | Science | Mankato | 575 | Transformers - 300 KVA & 225 KVA | The electrical system is equipped with two 300 KVA, 600V - 208Y/120V transformers; and two 225 KVA, 600V - 208Y/120V transformers located in the Main Electrical Vault. | 1982 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2032 | 2026 | 1 | 14 | Each | 9358.58 | 1.25 | 1.3 | 1.25 | 1 | 212907.7 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 14 | Each | 9358.58 | 266134.62 | 0 | 7142.86% | 10000 | 0 | Academic | South
| 547 | 04.750 | 7 | Science | Mankato | 586 | Water Heater - Elec - 20 Gallon | The domestic hot water is provided by a 76 Liter (20-gal), John Wood, electric, water heater rated at 1,500 W. | 2012 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2032 | 2026 | 1 | 1 | Each | 5615.61 | 1.25 | 1.3 | 1.25 | 1 | 9125.37 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 5615.61 | 11406.71 | 0 | 100000% | 10000 | 0 | Academic | South
| 511 | 04.750 | 7 | Science | Mankato | 549 | Wet Standpipe System | The fire protection systems include a wet fire standpipe system with backflow protection, distribution piping and shutoff valves. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 46220 | SF Building | 2.43 | 1.25 | 1.3 | 1.25 | 1 | 182511.23 | D402001 | Standpipes | Standpipes | Life Cycle Replacement | Active | Replace Standpipes | Priority 4: Proactive Replacement | 0 | 2026 | 46220 | SF Building | 2.43 | 228139.03 | 0 | 2.16% | 10000 | 0 | Academic | South
| 587 | 03.521 | 8 | Sports and Health Ctr | Eagan | 635 | Branch Wiring - Equipment & Devices | Branch wiring for the building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 19257 | SF Building | 8.66 | 1.25 | 1.3 | 1.05 | 1 | 227635.07 | D502001 | Branch Wiring and Devices | Branch Wiring and Devices | Life Cycle Replacement | Active | Replace Branch Wiring and Devices | Priority 4: Proactive Replacement | 0 | 2026 | 19257 | SF Building | 8.66 | 284543.84 | 0 | 5.19% | 10000 | 0 | Athletics | North
| 615 | 03.521 | 8 | Sports and Health Ctr | Eagan | 670 | Chilled Water Piping | The building is provided with chilled water piping and pumps. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 45 | 2017 | 2026 | 1 | 37954 | SF Building | 5.51 | 1.25 | 1.3 | 1.05 | 1 | 285457.73 | D304006 | Chilled Water Distribution Systems | Chilled Water Distribution Systems | Life Cycle Replacement | Active | Replace Chilled Water Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 37954 | SF Building | 5.51 | 356822.16 | 0 | 2.63% | 10000 | 0 | Athletics | North
| 602 | 03.521 | 8 | Sports and Health Ctr | Eagan | 651 | DDC/Pneumatic System - Hybrid | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities with pneumatic activation of control valves and dampers. | 1982 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2002 | 2026 | 1 | 68781 | SF Building | 2.79 | 1.25 | 1.3 | 1.05 | 1 | 261942.12 | D306006 | Direct Digital Control Systems | Direct Digital Control Systems | Life Cycle Replacement | Active | Replace Direct Digital Control Systems | Priority 4: Proactive Replacement | 0 | 2026 | 68781 | SF Building | 2.79 | 327427.65 | 0 | 1.45% | 10000 | 0 | Athletics | North
| 604 | 03.521 | 8 | Sports and Health Ctr | Eagan | 653 | Distribution Switchgears - 15kV, 600A | The electrical distribution system for the building is provided with a 600A,15kV, switchgear which includes fused, 3-Pole, Kirk Inter-locked, interrupter switches and incoming feeder. | 1982 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2022 | 2026 | 1 | 68781 | SF Building | 2.79 | 1.25 | 1.3 | 1.05 | 1 | 261942.12 | D501021 | Low Voltage Electrical Service | Low Voltage Electrical Service | Life Cycle Replacement | Active | Replace Low Voltage Electrical Service | Priority 4: Proactive Replacement | 0 | 2026 | 68781 | SF Building | 2.79 | 327427.65 | 0 | 1.45% | 10000 | 0 | Athletics | North
| 569 | 03.521 | 8 | Sports and Health Ctr | Eagan | 615 | Domestic Water Distribution | The building is provided with a water distribution system which includes a 4&rdquo; main pipe, water meter, branch piping, valves, insulation and fittings. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 35779 | SF Building | 3.65 | 1.25 | 1.3 | 1.05 | 1 | 178259.92 | D202001 | Domestic Water Piping and Fittings | Domestic Water Piping and Fittings | Life Cycle Replacement | Active | Replace Domestic Water Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 3.65 | 222824.9 | 0 | 2.79% | 10000 | 0 | Athletics | North
| 606 | 03.521 | 8 | Sports and Health Ctr | Eagan | 657 | Exterior Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1994 | 2019-11-07 | 2 - Good | The windows are in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 35 | 2029 | 2026 | 1 | 1722 | SF | 82.62 | 1.25 | 1.3 | 1.05 | 1 | 194200.79 | B202001 | Windows | Windows | Life Cycle Replacement | Active | Replace Windows | Priority 4: Proactive Replacement | 48 | 2026 | 1722 | SF | 82.62 | 242750.99 | 0 | 58.07% | 10000 | 0 | Athletics | North
| 597 | 03.521 | 8 | Sports and Health Ctr | Eagan | 646 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | The interior doors include hollow metal double doors with vision panels. | 1982 | 2019-11-07 | 2 - Good | The interior doors are in a fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 30 | 2012 | 2026 | 1 | 24 | Each | 5615.61 | 1.25 | 1.3 | 1.05 | 1 | 183967.38 | C102024 | Interior - Double Door - Hollow Metal | Interior - Double Door - Hollow Metal | Life Cycle Replacement | Active | Replace Interior - Double Door - Hollow Metal | Priority 4: Proactive Replacement | 31 | 2026 | 24 | Each | 5615.61 | 229959.23 | 0 | 4166.67% | 10000 | 0 | Athletics | North
| 590 | 03.521 | 8 | Sports and Health Ctr | Eagan | 638 | Interior Hollow Metal Swing Doors - Single Leaf - Rated | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 75 | Each | 2527.14 | 1.25 | 1.3 | 1.05 | 1 | 258715.96 | C102022 | Interior - Single Door - Wood | Interior - Single Door - Wood | Life Cycle Replacement | Active | Replace Interior - Single Door - Wood | Priority 4: Proactive Replacement | 31 | 2026 | 75 | Each | 2527.14 | 323394.95 | 0 | 1333.33% | 10000 | 0 | Athletics | North
| 600 | 03.521 | 8 | Sports and Health Ctr | Eagan | 649 | Lab Acid Waste System - Glass Pipe | The building includes an acid waste water glass piping system for the laboratories. | 1984 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2014 | 2026 | 1 | 23681 | SF | 7.3 | 1.25 | 1.3 | 1.05 | 1 | 235969.32 | D209002 | Acid Waste Systems | Acid Waste Systems | Life Cycle Replacement | Active | Replace Acid Waste Systems | Priority 4: Proactive Replacement | 0 | 2026 | 23681 | SF | 7.3 | 294961.66 | 0 | 4.22% | 10000 | 0 | Athletics | North
| 582 | 03.521 | 8 | Sports and Health Ctr | Eagan | 630 | Metal Wall Louvers | The building's exterior wall includes mechanical metal louvers located on the north side of the building. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 50 | 2022 | 2026 | 1 | 2153 | SF | 60.88 | 1.25 | 1.3 | 1.05 | 1 | 178916.88 | B201005 | Exterior Louvers and Screens | Exterior Louvers and Screens | Life Cycle Replacement | Active | Replace Exterior Louvers and Screens | Priority 4: Proactive Replacement | 44 | 2026 | 2153 | SF | 60.88 | 223646.1 | 0 | 46.45% | 10000 | 0 | Athletics | North
| 572 | 03.521 | 8 | Sports and Health Ctr | Eagan | 618 | Painted Wall Finish | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2010 | 2019-11-07 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 10 | 2020 | 2026 | 1 | 46220 | SF Building | 3.65 | 1.25 | 1.3 | 1.05 | 1 | 230279.6 | C301005 | Painted Wall Covering | Painted Wall Covering | Life Cycle Replacement | Active | Replace Painted Wall Covering | Priority 4: Proactive Replacement | 31 | 2026 | 46220 | SF Building | 3.65 | 287849.49 | 0 | 2.16% | 10000 | 0 | Athletics | North
| 575 | 03.521 | 8 | Sports and Health Ctr | Eagan | 622 | Painted Wall Finish | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2005 | 2019-11-07 | 2 - Good | The painted wall finish is in good condition overall. Lifecycle replacement can be deferred. | 10 | 2015 | 2026 | 1 | 63701 | SF Building | 3.65 | 1.25 | 1.3 | 1.05 | 1 | 317374.31 | C301005 | Painted Wall Covering | Painted Wall Covering | Life Cycle Replacement | Active | Replace Painted Wall Covering | Priority 4: Proactive Replacement | 31 | 2026 | 63701 | SF Building | 3.65 | 396717.88 | 0 | 1.57% | 10000 | 0 | Athletics | North
| 601 | 03.521 | 8 | Sports and Health Ctr | Eagan | 650 | Perimeter Heat - Electric Baseboard | HVAC distribution includes electric baseboard heating in the washrooms and corridors. | 1982 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2000 | 2026 | 1 | 50 | Each | 293.37 | 1.25 | 1.3 | 1.05 | 10 | 200225.03 | D305010 | Electric Baseboard Heaters | Electric Baseboard Heaters | Life Cycle Replacement | Active | Replace Electric Baseboard Heaters | Priority 4: Proactive Replacement | 0 | 2026 | 50 | Each | 293.37 | 250281.28 | 0 | 2000% | 10000 | 0 | Athletics | North
| 570 | 03.521 | 8 | Sports and Health Ctr | Eagan | 616 | Sanitary Waste - Gravity Discharge | The building is provided with a sanitary waste system which consists of cast iron, copper and PVC piping, as well as gravity discharge to the municipal system. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 35779 | SF Building | 4.15 | 1.25 | 1.3 | 1.05 | 1 | 202679.09 | D203001 | Sanitary Waste and Vent Piping and Fittings | Sanitary Waste and Vent Piping and Fittings | Life Cycle Replacement | Active | Replace Sanitary Waste and Vent Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 4.15 | 253348.86 | 0 | 2.79% | 10000 | 0 | Athletics | North
| 573 | 03.521 | 8 | Sports and Health Ctr | Eagan | 620 | Sanitary Waste - Gravity Discharge | The building is provided with a sanitary waste system of cast iron, copper and PVC piping with gravity discharge to the municipal system. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 46220 | SF Building | 4.15 | 1.25 | 1.3 | 1.05 | 1 | 261824.75 | D203001 | Sanitary Waste and Vent Piping and Fittings | Sanitary Waste and Vent Piping and Fittings | Life Cycle Replacement | Active | Replace Sanitary Waste and Vent Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 46220 | SF Building | 4.15 | 327280.93 | 0 | 2.16% | 10000 | 0 | Athletics | North
| 596 | 03.521 | 8 | Sports and Health Ctr | Eagan | 645 | Sanitary Waste - Gravity Discharge | The building includes a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 37594 | SF Building | 4.15 | 1.25 | 1.3 | 1.05 | 1 | 212960.61 | D203001 | Sanitary Waste and Vent Piping and Fittings | Sanitary Waste and Vent Piping and Fittings | Life Cycle Replacement | Active | Replace Sanitary Waste and Vent Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 37594 | SF Building | 4.15 | 266200.76 | 0 | 2.66% | 10000 | 0 | Athletics | North
| 577 | 03.521 | 8 | Sports and Health Ctr | Eagan | 625 | Sanitary Waste - Gravity Discharge - 1972 | The building includes a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 40828 | SF Building | 4.15 | 1.25 | 1.3 | 1.05 | 1 | 231280.41 | D203001 | Sanitary Waste and Vent Piping and Fittings | Sanitary Waste and Vent Piping and Fittings | Life Cycle Replacement | Active | Replace Sanitary Waste and Vent Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 40828 | SF Building | 4.15 | 289100.52 | 0 | 2.45% | 10000 | 0 | Athletics | North
| 595 | 03.521 | 8 | Sports and Health Ctr | Eagan | 643 | SIngle door | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1972 | 2019-11-07 | 2 - Good | The interior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 59 | Each | 2527.14 | 1.25 | 1.3 | 1.05 | 1 | 203523.22 | C102022 | Interior - Single Door - Wood | Interior - Single Door - Wood | Life Cycle Replacement | Active | Replace Interior - Single Door - Wood | Priority 4: Proactive Replacement | 31 | 2026 | 59 | Each | 2527.14 | 254404.02 | 0 | 1694.92% | 10000 | 0 | Athletics | North
| 592 | 03.521 | 8 | Sports and Health Ctr | Eagan | 640 | Vinyl Tile Flooring - 1972 | The building's floor finish includes asbestos containing vinyl tiles. | 1972 | 2019-11-07 | 2 - Good | The vinyl tiles are in fair condition overall, lifecycle replacement can be deferred. | 15 | 1987 | 2026 | 1 | 12317 | SF | 9.08 | 1.25 | 1.3 | 1.05 | 1.5 | 228989.04 | C302022 | Vinyl Tile / Plank Floor | Vinyl Tile / Plank Floor | Life Cycle Replacement | Active | Replace Vinyl Tile / Plank Floor | Priority 4: Proactive Replacement | 31 | 2026 | 12317 | SF | 9.08 | 286236.3 | 0 | 8.12% | 10000 | 0 | Athletics | North
| 579 | 03.521 | 8 | Sports and Health Ctr | Eagan | 627 | Wet Standpipe System | The fire protection systems include a standpipe system which Includes distribution piping, fire hose and shutoff valves | 1972 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 63701 | SF Building | 2.43 | 1.25 | 1.3 | 1.05 | 1 | 211293.03 | D402001 | Standpipes | Standpipes | Life Cycle Replacement | Active | Replace Standpipes | Priority 4: Proactive Replacement | 0 | 2026 | 63701 | SF Building | 2.43 | 264116.29 | 0 | 1.57% | 10000 | 0 | Athletics | North
| 603 | 03.521 | 8 | Sports and Health Ctr | Eagan | 652 | Wet Standpipe System | The fire protection systems include a wet fire standpipe system which Includes distribution piping and shutoff valves | 1982 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2022 | 2026 | 1 | 68781 | SF Building | 2.43 | 1.25 | 1.3 | 1.05 | 1 | 228143.14 | D402001 | Standpipes | Standpipes | Life Cycle Replacement | Active | Replace Standpipes | Priority 4: Proactive Replacement | 0 | 2026 | 68781 | SF Building | 2.43 | 285178.92 | 0 | 1.45% | 10000 | 0 | Athletics | North
| 629 | 22.054 | 9 | The Oswald Visitor Center | Miami | 688 | Branch Wiring - Equipment & Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 35779 | SF Building | 8.66 | 1.25 | 1.3 | 1.15 | 1 | 463219.98 | D502001 | Branch Wiring and Devices | Branch Wiring and Devices | Life Cycle Replacement | Active | Replace Branch Wiring and Devices | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 8.66 | 579024.97 | 0 | 2.79% | 10000 | 0 | Operations | North
| 646 | 22.054 | 9 | The Oswald Visitor Center | Miami | 705 | Branch Wiring - Equipment & Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 27857 | SF Building | 8.66 | 1.25 | 1.3 | 1.15 | 1 | 360656.22 | D502001 | Branch Wiring and Devices | Branch Wiring and Devices | Life Cycle Replacement | Active | Replace Branch Wiring and Devices | Priority 4: Proactive Replacement | 0 | 2026 | 27857 | SF Building | 8.66 | 450820.28 | 0 | 3.59% | 10000 | 0 | Operations | North
| 644 | 22.054 | 9 | The Oswald Visitor Center | Miami | 703 | Central AHU | The HVAC system serving both the C-Block and the F-Block includes a central AHU with chilled water coils, and electric heating elements having a approximate capacity of approximately 20,000 CFM. It branches off into two separate streams and is located in the basement of F-Block. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 244462.68 | 1.25 | 1.3 | 1.15 | 1 | 365471.71 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | Air Handling Units - Built- Up - Over 20,000 CFM | Life Cycle Replacement | Active | Replace Air Handling Units - Built- Up - Over 20,000 CFM | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 244462.68 | 456839.63 | 0 | 100000% | 10000 | 0 | Operations | North
| 658 | 22.054 | 9 | The Oswald Visitor Center | Miami | 718 | Central AHU - Air Handler - 30000 CFM - HC-1 | The HVAC system has a central AHU with chilled water coils and hot water coils having a approximate capacity of 30000 CFM. | 1985 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. | 40 | 2025 | 2026 | 1 | 1 | Each | 244462.68 | 1.25 | 1.3 | 1.15 | 1 | 365471.71 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | Air Handling Units - Built- Up - Over 20,000 CFM | Life Cycle Replacement | Active | Replace Air Handling Units - Built- Up - Over 20,000 CFM | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 244462.68 | 456839.63 | 0 | 100000% | 10000 | 0 | Operations | North
| 639 | 22.054 | 9 | The Oswald Visitor Center | Miami | 698 | Central AHU - Air Handler - Electric Heat - Serves Both B and E Blocks | The HVAC system serving both the B-Block and the E-Block includes a central AHU with chilled water coils, and heating hot water coils having a capacity of approximately 30000 CFM. It branches off into two separate streams and is located in the basement of E-Block. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 244462.68 | 1.25 | 1.3 | 1.15 | 1 | 365471.71 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | Air Handling Units - Built- Up - Over 20,000 CFM | Life Cycle Replacement | Active | Replace Air Handling Units - Built- Up - Over 20,000 CFM | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 244462.68 | 456839.63 | 0 | 100000% | 10000 | 0 | Operations | North
| 652 | 22.054 | 9 | The Oswald Visitor Center | Miami | 711 | Central AHU - D and G Blocks | The HVAC system includes a 20,000 cfm, central AHU with chilled water coils and electric heating elements that serves both the D-Block and the G-Block. It branches off into two separate streams and is located in the basement of F-Block. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2012 | 2026 | 1 | 1 | Each | 244462.68 | 1.25 | 1.3 | 1.15 | 1 | 365471.71 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | Air Handling Units - Built- Up - Over 20,000 CFM | Life Cycle Replacement | Active | Replace Air Handling Units - Built- Up - Over 20,000 CFM | Priority 4: Proactive Replacement | 0 | 2026 | 1 | Each | 244462.68 | 456839.63 | 0 | 100000% | 10000 | 0 | Operations | North
| 656 | 22.054 | 9 | The Oswald Visitor Center | Miami | 716 | Domestic Water Distribution | The building water distribution system includes a 4&rdquo; for main branch piping, water meter, valves, insulation and fittings. | 1982 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40 | 2022 | 2026 | 1 | 61903 | SF Building | 3.65 | 1.25 | 1.3 | 1.15 | 1 | 337789.2 | D202001 | Domestic Water Piping and Fittings | Domestic Water Piping and Fittings | Life Cycle Replacement | Active | Replace Domestic Water Piping and Fittings | Priority 4: Proactive Replacement | 0 | 2026 | 61903 | SF Building | 3.65 | 422236.49 | 0 | 1.62% | 10000 | 0 | Operations | North
| 640 | 22.054 | 9 | The Oswald Visitor Center | Miami | 699 | Ductwork Distribution System | The HVAC system is provided with ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building.. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 19257 | SF Building | 10.94 | 1.25 | 1.3 | 1.15 | 1 | 314954.01 | D304001 | Air Distribution Systems | Air Distribution Systems | Life Cycle Replacement | Active | Replace Air Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 19257 | SF Building | 10.94 | 393692.52 | 0 | 5.19% | 10000 | 0 | Operations | North
| 627 | 22.054 | 9 | The Oswald Visitor Center | Miami | 686 | Eggcrate Ceiling - Exposed T-bar | The building's ceiling finishes include egg crate ceiling tiles located in the offices. | 1972 | 2019-11-06 | 2 - Good | The eggcrate ceiling is in good condition overall, no deficiencies were observed. lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 37017 | SF | 7.87 | 1.25 | 1.3 | 1.15 | 1 | 435529.07 | C303007 | Suspended Acoustic Ceiling Panels | Suspended Acoustic Ceiling Panels | Life Cycle Replacement | Active | Replace Suspended Acoustic Ceiling Panels | Priority 4: Proactive Replacement | 20 | 2026 | 37017 | SF | 7.87 | 544411.33 | 0 | 2.7% | 10000 | 0 | Operations | North
| 659 | 22.054 | 9 | The Oswald Visitor Center | Miami | 719 | Exhaust System - Fume Hoods | The HVAC ventilation system for the labs includes constant volume fume hoods with exhaust systems. | 1990 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25 | 2015 | 2026 | 1 | 120 | Each | 2808.19 | 1.25 | 1.3 | 1.15 | 1 | 503789.29 | D304031 | Exhaust Fans - Centrifugal | Exhaust Fans - Centrifugal | Life Cycle Replacement | Active | Replace Exhaust Fans - Centrifugal | Priority 4: Proactive Replacement | 0 | 2026 | 120 | Each | 2808.19 | 629736.61 | 0 | 833.33% | 10000 | 0 | Operations | North
| 680 | 22.054 | 9 | The Oswald Visitor Center | Miami | 742 | Heating Hot Water Piping | The HVAC system is provided with Heating Hot Water piping and pumps. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 45 | 2017 | 2026 | 1 | 37954 | SF Building | 8.23 | 1.25 | 1.3 | 1.15 | 1 | 466980.32 | D304003 | Heating Water Distribution Systems | Heating Water Distribution Systems | Life Cycle Replacement | Active | Replace Heating Water Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 37954 | SF Building | 8.23 | 583725.4 | 0 | 2.63% | 10000 | 0 | Operations | North
| 625 | 22.054 | 9 | The Oswald Visitor Center | Miami | 684 | Interior Hollow Metal Swing Doors - Single Leaf - Non rated | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 1972 | 2019-11-06 | 2 - Good | The interior doors are in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 120 | Each | 2527.14 | 1.25 | 1.3 | 1.15 | 1 | 453368.92 | C102022 | Interior - Single Door - Wood | Interior - Single Door - Wood | Life Cycle Replacement | Active | Replace Interior - Single Door - Wood | Priority 4: Proactive Replacement | 20 | 2026 | 120 | Each | 2527.14 | 566711.15 | 0 | 833.33% | 10000 | 0 | Operations | North
| 624 | 22.054 | 9 | The Oswald Visitor Center | Miami | 683 | Interior Windows - Metal | The building includes window units and storefront windows installed in partition openings located on the 400 floor level. | 1972 | 2019-11-06 | 2 - Good | No deficiencies were observed or reported. Lifecycle replacement can be deferred. | 75 | 2047 | 2026 | 1 | 4553 | SF | 52.22 | 1.25 | 1.3 | 1.15 | 1 | 355447.7 | C101005 | Interior Windows | Interior Windows | Life Cycle Replacement | Active | Replace Interior Windows | Priority 4: Proactive Replacement | 20 | 2026 | 4553 | SF | 52.22 | 444309.63 | 0 | 21.96% | 10000 | 0 | Operations | North
| 645 | 22.054 | 9 | The Oswald Visitor Center | Miami | 704 | Perimeter Heat - Electric Baseboard | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 1990 | 2026 | 1 | 1000 | Each | 293.37 | 1.25 | 1.3 | 1.15 | 1 | 438588.15 | D305010 | Electric Baseboard Heaters | Electric Baseboard Heaters | Life Cycle Replacement | Active | Replace Electric Baseboard Heaters | Priority 4: Proactive Replacement | 0 | 2026 | 1000 | Each | 293.37 | 548235.19 | 0 | 100% | 10000 | 0 | Operations | North
| 670 | 22.054 | 9 | The Oswald Visitor Center | Miami | 732 | Perimeter Heat - Electric Baseboard | The HVAC equipment includes electric baseboard heating in the exterior offices. | 2007 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2037 | 2026 | 1 | 6000 | LF | 80.03 | 1.25 | 1.3 | 1.15 | 0.5 | 358934.55 | D305004 | Finned Tube Radiation Units | Finned Tube Radiation Units | Life Cycle Replacement | Active | Replace Finned Tube Radiation Units | Priority 4: Proactive Replacement | 0 | 2026 | 6000 | LF | 80.03 | 448668.19 | 0 | 16.67% | 10000 | 0 | Operations | North
| 679 | 22.054 | 9 | The Oswald Visitor Center | Miami | 741 | Server room A/C | The IT server room is provided with two LIEBERT, 40 ton, DX, A/C units. | 1999 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 18 | 2017 | 2026 | 1 | 8 | Each | 37434.32 | 1.25 | 1.3 | 1.15 | 1 | 447714.47 | D303023 | Refrigerant DX Condensing Units - Over 20 Tons | Refrigerant DX Condensing Units - Over 20 Tons | Life Cycle Replacement | Active | Replace Refrigerant DX Condensing Units - Over 20 Tons | Priority 4: Proactive Replacement | 0 | 2026 | 8 | Each | 37434.32 | 559643.08 | 0 | 12500% | 10000 | 0 | Operations | North
| 620 | 22.054 | 9 | The Oswald Visitor Center | Miami | 679 | Water Heater - Elec - Residential - 40 Gallon | The domestic hot water is provided by a 151 Liter (40-gallon), electric, water heater rated at 3000 W | 2010 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2030 | 2026 | 1 | 2 | Each | 5615.61 | 1.25 | 1.3 | 1.15 | 1 | 16790.67 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 5615.61 | 20988.34 | 0 | 50000% | 10000 | 0 | Operations | North
| 677 | 22.054 | 9 | The Oswald Visitor Center | Miami | 739 | Water Tank Heater - 2005 | The water distribution system is provided with a RHEEM, 175 Liter (46 gal), electric, water tank heater. | 2005 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 20 | 2025 | 2026 | 1 | 2 | Each | 5615.61 | 1.25 | 1.3 | 1.15 | 1 | 16790.67 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 5615.61 | 20988.34 | 0 | 50000% | 10000 | 0 | Operations | North
| 678 | 22.054 | 9 | The Oswald Visitor Center | Miami | 740 | Water Tank Heater - 2011 | The water distribution system is provided with a JOHN WOOD, 184 Liter (48 gal), electric, water tank heater. | 2011 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred | 20 | 2031 | 2026 | 1 | 2 | Each | 5615.61 | 1.25 | 1.3 | 1.15 | 1 | 16790.67 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic Water Conditioners - Water Softener Systems | Life Cycle Replacement | Active | Replace Domestic Water Conditioners - Water Softener Systems | Priority 4: Proactive Replacement | 0 | 2026 | 2 | Each | 5615.61 | 20988.34 | 0 | 50000% | 10000 | 0 | Operations | North
| 717 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 782 | Acoustic Tile Ceiling - Exposed T-bar - 1997 | The building's ceiling finishes include acoustic ceiling tiles with T-bar suspension system. | 1997 | 2019-11-06 | 2 - Good | The ceiling tiles are in good condition overall, lifecycle replacement can be deferred. | 30 | 2027 | 2026 | 1 | 79653 | SF | 6.15 | 1.25 | 1.3 | 1.15 | 1 | 732349.6 | C303004 | Adhered Acoustic Tile Ceiling | Adhered Acoustic Tile Ceiling | Life Cycle Replacement | Active | Replace Adhered Acoustic Tile Ceiling | Priority 4: Proactive Replacement | 27 | 2026 | 79653 | SF | 6.15 | 915436.99 | 0 | 1.26% | 10000 | 0 | Academic | West
| 709 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 774 | Branch Wiring - Equipment & Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 46220 | SF Building | 8.66 | 1.25 | 1.3 | 1.15 | 1 | 598396.47 | D502001 | Branch Wiring and Devices | Branch Wiring and Devices | Life Cycle Replacement | Active | Replace Branch Wiring and Devices | Priority 4: Proactive Replacement | 0 | 2026 | 46220 | SF Building | 8.66 | 747995.59 | 0 | 2.16% | 10000 | 0 | Academic | West
| 727 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 792 | Branch Wiring - Equipment & Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 37954 | SF Building | 8.66 | 1.25 | 1.3 | 1.15 | 1 | 491379.05 | D502001 | Branch Wiring and Devices | Branch Wiring and Devices | Life Cycle Replacement | Active | Replace Branch Wiring and Devices | Priority 4: Proactive Replacement | 0 | 2026 | 37954 | SF Building | 8.66 | 614223.81 | 0 | 2.63% | 10000 | 0 | Academic | West
| 720 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 785 | Branch Wiring - Equipment & Devices - Average Density - 1972 | Branch wiring for the 1972 section of the building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 40828 | SF Building | 8.66 | 1.25 | 1.3 | 1.15 | 1 | 528587.87 | D502001 | Branch Wiring and Devices | Branch Wiring and Devices | Life Cycle Replacement | Active | Replace Branch Wiring and Devices | Priority 4: Proactive Replacement | 0 | 2026 | 40828 | SF Building | 8.66 | 660734.83 | 0 | 2.45% | 10000 | 0 | Academic | West
| 700 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 765 | Ductwork Distribution System | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 35779 | SF Building | 10.94 | 1.25 | 1.3 | 1.15 | 1 | 585176.28 | D304001 | Air Distribution Systems | Air Distribution Systems | Life Cycle Replacement | Active | Replace Air Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 35779 | SF Building | 10.94 | 731470.35 | 0 | 2.79% | 10000 | 0 | Academic | West
| 724 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 789 | Ductwork Distribution System | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 27857 | SF Building | 10.94 | 1.25 | 1.3 | 1.15 | 1 | 455609.59 | D304001 | Air Distribution Systems | Air Distribution Systems | Life Cycle Replacement | Active | Replace Air Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 27857 | SF Building | 10.94 | 569511.99 | 0 | 3.59% | 10000 | 0 | Academic | West
| 726 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 791 | Ductwork Distribution System | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 37954 | SF Building | 10.94 | 1.25 | 1.3 | 1.15 | 1 | 620749.06 | D304001 | Air Distribution Systems | Air Distribution Systems | Life Cycle Replacement | Active | Replace Air Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 37954 | SF Building | 10.94 | 775936.32 | 0 | 2.63% | 10000 | 0 | Academic | West
| 719 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 784 | Ductwork Distribution System - 1972 | The HVAC system for the 1972 section of the building includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 40828 | SF Building | 10.94 | 1.25 | 1.3 | 1.15 | 1 | 667754.19 | D304001 | Air Distribution Systems | Air Distribution Systems | Life Cycle Replacement | Active | Replace Air Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 40828 | SF Building | 10.94 | 834692.74 | 0 | 2.45% | 10000 | 0 | Academic | West
| 744 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 819 | HHW Piping | The HVAC system is provided with heating hot water (HHW) piping, valves and pumps. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 45 | 2017 | 2026 | 1 | 63701 | SF Building | 8.23 | 1.25 | 1.3 | 1.15 | 1 | 783767.55 | D304003 | Heating Water Distribution Systems | Heating Water Distribution Systems | Life Cycle Replacement | Active | Replace Heating Water Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 63701 | SF Building | 8.23 | 979709.44 | 0 | 1.57% | 10000 | 0 | Academic | West
| 707 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 772 | Interior Hollow Metal Swing Doors - Single Leaf - Nonrated | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 135 | Each | 2527.14 | 1.25 | 1.3 | 1.15 | 1 | 510040.03 | C102022 | Interior - Single Door - Wood | Interior - Single Door - Wood | Life Cycle Replacement | Active | Replace Interior - Single Door - Wood | Priority 4: Proactive Replacement | 27 | 2026 | 135 | Each | 2527.14 | 637550.04 | 0 | 740.74% | 10000 | 0 | Academic | West
| 706 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 771 | Interior Windows - Metal | The building includes window units and storefront windows installed in partition openings located on the 400 and 300 floors. | 1972 | 2019-11-06 | 2 - Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 75 | 2047 | 2026 | 1 | 10010 | SF | 52.22 | 1.25 | 1.3 | 1.15 | 1 | 781469.69 | C101005 | Interior Windows | Interior Windows | Life Cycle Replacement | Active | Replace Interior Windows | Priority 4: Proactive Replacement | 27 | 2026 | 10010 | SF | 52.22 | 976837.11 | 0 | 9.99% | 10000 | 0 | Academic | West
| 718 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 783 | Lab Acid Waste System - Glass Pipe | The building includes a acid water waste glass piping system for the laboratories. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 30 | 2002 | 2026 | 1 | 50773 | SF | 7.3 | 1.25 | 1.3 | 1.15 | 1 | 554111.14 | D209002 | Acid Waste Systems | Acid Waste Systems | Life Cycle Replacement | Active | Replace Acid Waste Systems | Priority 4: Proactive Replacement | 0 | 2026 | 50773 | SF | 7.3 | 692638.92 | 0 | 1.97% | 10000 | 0 | Academic | West
| 745 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 820 | Main Electrical System Transformer | The electrical system for the building is provided with a 2500 kVA, 13.8kV - 600Y/347V, main transformer. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 35 | Each | 9358.58 | 1.25 | 1.3 | 1.15 | 1 | 489687.7 | D501026 | Grounding Methods | Grounding Methods | Life Cycle Replacement | Active | Replace Grounding Methods | Priority 4: Proactive Replacement | 0 | 2026 | 35 | Each | 9358.58 | 612109.62 | 0 | 2857.14% | 10000 | 0 | Academic | West
| 715 | 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 780 | Single door | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on metal frames. | 1972 | 2019-11-06 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review. Lifecycle replacement can be deferred. | 25 | 1997 | 2026 | 1 | 165 | Each | 2527.14 | 1.25 | 1.3 | 1.15 | 1 | 623382.26 | C102022 | Interior - Single Door - Wood | Interior - Single Door - Wood | Life Cycle Replacement | Active | Replace Interior - Single Door - Wood | Priority 4: Proactive Replacement | 27 | 2026 | 165 | Each | 2527.14 | 779227.82 | 0 | 606.06% | 10000 | 0 | Academic | West
| 788 | 01.204 | 11 | Wilson Library | Cottage Grove | 881 | Branch Wiring - Equipment & Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1982 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2032 | 2026 | 1 | 68781 | SF Building | 8.66 | 1.25 | 1.3 | 1 | 1 | 774336.5 | D502001 | Branch Wiring and Devices | Branch Wiring and Devices | Life Cycle Replacement | Active | Replace Branch Wiring and Devices | Priority 4: Proactive Replacement | 0 | 2026 | 68781 | SF Building | 8.66 | 967920.62 | 0 | 1.45% | 10000 | 0 | Operations | Central
| 775 | 01.204 | 11 | Wilson Library | Cottage Grove | 862 | Ductwork Distribution System | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | 2022 | 2026 | 1 | 46220 | SF Building | 10.94 | 1.25 | 1.3 | 1 | 1 | 657340.84 | D304001 | Air Distribution Systems | Air Distribution Systems | Life Cycle Replacement | Active | Replace Air Distribution Systems | Priority 4: Proactive Replacement | 0 | 2026 | 46220 | SF Building | 10.94 | 821676.05 | 0 | 2.16% | 10000 | 0 | Operations | Central
| 776 | 01.204 | 11 | Wilson Library | Cottage Grove | 865 | Exterior windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1972 | 2019-11-04 | 2 - Good | The windows have aged but are in fair condition overall, lifecycle replacement can be deferred. | 35 | 2007 | 2026 | 1 | 34445 | SF | 82.62 | 1.25 | 1.3 | 1 | 1 | 3699599.67 | B202001 | Windows | Windows | Life Cycle Replacement | Active | Replace Windows | Priority 4: Proactive Replacement | 52 | 2026 | 34445 | SF | 82.62 | 4624499.59 | 0 | 2.9% | 10000 | 0 | Operations | Central
| 780 | 01.204 | 11 | Wilson Library | Cottage Grove | 869 | Exterior Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1972 | 2019-11-04 | 2 - Good | The windows have aged but are in fair condition overall, lifecycle replacement can be deferred. | 35 | 2007 | 2026 | 1 | 35521 | SF | 82.62 | 1.25 | 1.3 | 1 | 1 | 3815168.53 | B202001 | Windows | Windows | Life Cycle Replacement | Active | Replace Windows | Priority 4: Proactive Replacement | 52 | 2026 | 35521 | SF | 82.62 | 4768960.66 | 0 | 2.82% | 10000 | 0 | Operations | Central
| 784 | 01.204 | 11 | Wilson Library | Cottage Grove | 873 | Exterior windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1972 | 2019-11-04 | 2 - Good | The windows have aged but are in fair condition overall, lifecycle replacement can be deferred. | 35 | 2007 | 2026 | 1 | 11814 | SF | 82.62 | 1.25 | 1.3 | 1 | 1 | 1268894.48 | B202001 | Windows | Windows | Life Cycle Replacement | Active | Replace Windows | Priority 4: Proactive Replacement | 52 | 2026 | 11814 | SF | 82.62 | 1586118.11 | 0 | 8.46% | 10000 | 0 | Operations | Central