## Overview
SLAMUSA_Elements
Generated on | March 24, 2026
Generated for | SLAM USA
Generated by | Bill Roth
Asset | - All -
Uniformat Code | - All -
Condition | - All -
Status | Active

## Data
Flags | Facility # | Asset ID | Asset Name | City | Element ID | Element Descriptor | Uniformat Code | Uniformat Name | Description | Year Installed | Expected Useful Life | Expected Renewal Year | Observed Renewal Year | Last Assessment | Condition | Condition Narrative | Quantity | Units | Unit Cost | Soft Cost Factor | Regional Factor | Difficulty Factor | Element Cost | Recommendation Count | Element Status | Imported Element ID | Asset Tag # | Warranty Expiration Date | Work Day # | Asset Type | Zone
| 04.758 | 1 | Humanities Fine Arts | Morris | 125 | Acoustic Ceiling Tiles | C303007 | Suspended Acoustic Ceiling Panels | The building's ceiling finishes include acoustic ceiling tiles located on the 100 floor outside J201 | 2016 | 25 | 2041 | 2036 | 2019-10-15 | 1 - Excellent | The ceiling finish is in good condition overall, no significant deficiencies were observed. | 840 | SF | 7.87 | 1.3 | 1.25 | 1 | 10742.55 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 100 | Acoustic Tile Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | Ceiling finishes located in some offices and laboratories include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 1994 | 25 | 2019 | 2014 | 2019-10-15 | 5 - Critical | The ceiling tiles in the second floor are in poor condition, lifecycle replacement is recommended. | 180 | SF | 7.87 | 1.3 | 1.25 | 1 | 2301.98 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 18 | Air Handling Unit - Wine Cellar | D304011 | Refrigerant Distribution Systems | The HVAC system includes an air handling unit with a cooling capacity of 5 tons for the wine cellar with chilled water cooling coils. | 1998 | 45 | 2043 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 14500 | SF | 4.36 | 1.3 | 1.25 | 1 | 102732.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 136 | Aluminum Framed IGUs | B202001 | Windows | The building includes punched windows with aluminum frames and insulated glazing units in stone cladding. | 2021 | 35 | 2056 | 2050 | 2019-10-15 | 1 - Excellent |  | 8 | SF | 82.62 | 1.3 | 1.25 | 1 | 1074.06 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 135 | B301025 - Inverted - Modified Bitumen | B301025 | Inverted - Modified Bitumen | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2021 | 30 | 2051 | 2051 | 2019-10-15 | 1 - Excellent |  | 300 | SF | 20.03 | 1.3 | 1.25 | 1 | 9764.63 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 132 | B301028 Metal Roofing | B301028 | Metal Roofing | The gable (or hip) roof structure cover is a standing seam (or R-panel) prefinished metal roof. At the roof edge, gutters connected to downspouts that discharge to grade or stormwater sewer system are provided. Add where applicable Ice/snow stops are provided to mitigate the effects of forming ice dams above the main entrance. At the time of the assessment, no roof leaks were reported, and no corrosion or deteriorated metal roof panels were observed. According to information provided, the roof metal panels were replaced in approximately xxxx, and based on age and expected useful life of approximately 30 years, the prefinished metal roof estimated remaining useful life is approximately xx years. OR During the assessment corrosion was observed on the metal roof panels. Based on the observed condition the roof is estimated to have a remaining useful life of approximately xx years | 2015 | 40 | 2055 | 2025 | 2019-10-15 | 2 - Good | It's Good | 125 | SF | 24.39 | 1.3 | 1.25 | 1.5 | 7431.33 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 134 | B301028 Metal Roofing | B301028 | Metal Roofing | The gable (or hip) roof structure cover is a standing seam (or R-panel) prefinished metal roof. At the roof edge, gutters connected to downspouts that discharge to grade or stormwater sewer system are provided. Add where applicable Ice/snow stops are provided to mitigate the effects of forming ice dams above the main entrance. At the time of the assessment, no roof leaks were reported, and no corrosion or deteriorated metal roof panels were observed. According to information provided, the roof metal panels were replaced in approximately xxxx, and based on age and expected useful life of approximately 30 years, the prefinished metal roof estimated remaining useful life is approximately xx years. OR During the assessment corrosion was observed on the metal roof panels. Based on the observed condition the roof is estimated to have a remaining useful life of approximately xx years | 2021 | 40 | 2061 | 2055 | 2019-10-15 | 1 - Excellent |  | 125 | SF | 24.39 | 1.3 | 1.25 | 1.5 | 7431.33 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 133 | B301030 - Slate Roofing | B301030 | Slate Roofing | Slate Roof. | 2022 | 50 | 2072 | 2097 | 2019-10-15 | 1 - Excellent |  | 125 | SF | 30.47 | 1.3 | 1.25 | 1.2 | 7427.06 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 93 | Boiler HW - 1982 | D302002 | Hot Water Boilers - Up to 1000 MBH | Heating Hot Water is provided from a Chromalox electric steam boiler rated at 82 MBH (24 KW). | 1982 | 30 | 2012 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 82 | MBH | 70.84 | 1.3 | 1.25 | 1 | 9439.43 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 94 | Boiler HW - 1990 | D302002 | Hot Water Boilers - Up to 1000 MBH | Heating medium is provided from a Caloritech electric steam boiler rated at approximately 40 MBH (12 kW). | 1990 | 30 | 2020 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 41 | MBH | 70.84 | 1.3 | 1.25 | 1 | 4719.72 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 138 | C301005 - Painted Wall Covering | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2023 | 10 | 2033 | 2033 | 2019-10-15 | 1 - Excellent |  | 1120 | SF Building | 3.65 | 1.3 | 1.25 | 1 | 6643 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 141 | C302004 - Vinyl Tile | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include carpet tile flooring located in offices, conference rooms and miscellaneous spaces. | 2023 | 15 | 2038 | 2038 | 2019-10-15 | 1 - Excellent |  | 500 | SF | 9.08 | 1.3 | 1.25 | 1 | 7377.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 139 | C302005 - Carpet | C302005 | Carpet Floor | The building's floor finish includes asbestos containing vinyl tiles. | 2023 | 10 | 2033 | 2033 | 2019-10-15 | 1 - Excellent |  | 600 | SF | 7.87 | 1.3 | 1.25 | 1.5 | 11509.88 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 140 | C302005 - Carpet | C302005 | Carpet Floor | The building's floor finishes include vinyl floor tiles located in the labs and the hall ways. | 2023 | 10 | 2033 | 2033 | 2019-10-15 | 1 - Excellent |  | 860 | SF | 7.87 | 1.3 | 1.25 | 1 | 10998.33 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 928 | C302005 - Carpet Floor | C302005 | Carpet Floor | Carpet | 2025 | 10 | 2035 | 2035 |  | 1 - Excellent |  | 1368 | SF | 7.87 | 1.3 | 1.25 | 1 | 17495.01 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 905 | C302007 - Painted / Sealed Floor | C302007 | Painted / Sealed Floor | The building's floor finishes include painted floor finish located at 500 floor storage room and electrical rooms. | 2025 | 15 | 2040 | 2040 |  | 2 - Good | Newly Painted in 2025 - Excellent | 870 | SF | 3.65 | 1.3 | 1.25 | 1 | 5160.19 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 899 | C303006 - Painted Ceiling Structures | C303006 | Painted Ceiling Structures | Ceiling finishes located in some offices and laboratories include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2023 | 15 | 2038 | 2038 |  | 5 - Critical |  | 200 | SF | 2.65 | 1.3 | 1.25 | 1 | 861.25 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 16 | Central AHU 1 - Air Handler - TRANE | D304011 | Refrigerant Distribution Systems | The HVAC system has a central air handling unit, AHU-1, with chilled water coils, hot water coils and steam humidification having a approximate capacity of 15000 CFM. | 1998 | 45 | 2043 | 2028 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. | 14500 | SF | 4.36 | 1.3 | 1.25 | 1 | 102732.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 110 | Ceramic Tile Flooring | C302001 | Ceramic Tile Floor | The building's floor finishes include ceramic tile and base provided in the laundry room. | 2007 | 40 | 2047 | 2037 | 2019-10-15 | 1 - Excellent | The ceramic floor finish is in good condition overall. | 54 | SF | 15.67 | 1.3 | 1.25 | 1 | 1375.04 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 126 | Coffin door roof hatch | B302023 | Hatches | Hollow metal coffin door provides access to building&rsquo;s roof. | 2007 | 40 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | The roof access door is in good condition overall, no major deficiencies were observed. | 1 | Each | 2720.41 | 1.3 | 1.25 | 1 | 4420.67 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 131 | Concrete stairs | C201001 | Interior Stair Construction | The building includes concrete infilled metal framed stairs with ceramic tile finish that provide access to the 3rd and 4th floors. | 2007 | 75 | 2082 | 2082 | 2019-10-15 | 1 - Excellent | The interior stairs are in good condition overall. | 80 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 97397.3 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 8 | Custodial Sinks | D201004 | Sinks | The plumbing fixtures include floor mounted custodial sinks. | 2012 | 35 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 977.9 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 64 | Custodial Sinks | D201016 | Custodial Sinks | The plumbing fixtures include custodial sinks installed on two floors. | 2000 | 30 | 2030 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 1955.8 | 1.3 | 1.25 | 1 | 6356.35 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 117 | Custodial Sinks | D201016 | Custodial Sinks | The plumbing fixtures include flooor-mounted custodial sinks. | 1972 | 30 | 2002 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 1955.8 | 1.3 | 1.25 | 1 | 9534.53 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 913 | Custodial Sinks | D201004 | Sinks | The plumbing fixtures include floor mounted custodial sinks. | 2025 | 35 | 2060 | 2060 |  | 1 - Excellent |  | 1 | Each | 977.9 | 1.3 | 1.25 | 1 | 1589.09 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 82 | Custodial Sinks - 1972 | D201016 | Custodial Sinks | The plumbing fixtures include custodial sinks. | 1972 | 30 | 2002 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 1955.8 | 1.3 | 1.25 | 1 | 6356.35 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 79 | Custodial Sinks - 2000 | D201016 | Custodial Sinks | The plumbing fixtures include a custodial sink installed on the 2nd floor. | 2000 | 30 | 2030 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred | 1 | Each | 1955.8 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 13 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include a custodial/utility sink installed in the janitor closet. | 1998 | 30 | 2028 | 2025 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 1955.8 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 26 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include a custodial sink installed on the 2nd floor. | 2000 | 30 | 2030 | 2025 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 1955.8 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 37 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include a custodial/utility sink installed on the 3rd floor. | 2000 | 30 | 2030 | 2025 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 1955.8 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 57 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include a floor mounted custodial sink on the 3rd floor. | 2000 | 30 | 2030 | 2025 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 1955.8 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 92 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include custodial/utility sink in the janitor's closet on each floor. | 1990 | 30 | 2020 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 1955.8 | 1.3 | 1.25 | 1 | 6356.35 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 7 | Dock Leveller | E109099 | Other Equipment (Other) | The loading dock is provided with a Blue Giant, 6,000LB, dock leveller. | 2012 | 25 | 2037 | 2037 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 1 | Lump Sum | 3850 | 1.3 | 1.25 | 1 | 6256.25 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 83 | Drinking Water Fountains | D201006 | Drinking Water Fountains (Non-refrigerated) | Plumbing fixtures include wall mounted stainless steel drinking water fountains in the corridors. | 1990 | 30 | 2020 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 1466.85 | 1.3 | 1.25 | 1 | 4767.26 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 916 | DX Ductless Split Refrigerant Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for each of the cold rooms is provided by a 2 ton ductless split DX refrigerant unit. | 2025 | 18 | 2043 | 2043 |  | 2 - Good |  | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 68 | DX Ductless Split Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for the Main Electrical Vault is provided by a 2 ton ductless split DX unit. | 2008 | 18 | 2026 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 84 | DX Ductless Split Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for the walk in cooler is provided by a 2 ton ductless split DX refrigerant unit. | 2008 | 18 | 2026 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 104 | DX Ductless Split Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for some of the rooms requiring special climate control is provided by a 2 ton Carrier ductless split DX unit. | 2008 | 18 | 2026 | 2025 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 53 | Epoxy Flooring | C302007 | Painted / Sealed Floor | The building's floor finishes include epoxy floor finish located in room E304. | 2000 | 15 | 2015 | 2015 | 2019-10-15 | 5 - Critical | The epoxy floor is in poor condition, lifecycle replacement is recommended. | 754 | SF | 3.65 | 1.3 | 1.25 | 1 | 4472.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 137 | Epoxy Wall Paint | C301005 | Painted Wall Covering | The building&rsquo;s wall finishes include epoxy paint finish located in the Phytotron, CL3, and, animal lab areas. | 2023 | 10 | 2033 | 2033 | 2019-10-15 | 1 - Excellent |  | 600 | SF Building | 3.65 | 1.3 | 1.25 | 1 | 3558.75 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 69 | Exhaust System - Fume Hood | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1990 | 25 | 2015 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 4679.29 | 1.3 | 1.25 | 1 | 15207.69 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 27 | Exhaust System - Fume Hood - Ductwork/Fan | E102007 | Fume Hood Systems | The exhaust system for the labs includes constant volume fume hoods and exhaust systems. | 1990 | 25 | 2015 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 4679.29 | 1.3 | 1.25 | 1 | 15207.69 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 95 | Exhaust System Fans | D304031 | Exhaust Fans - Centrifugal | The HVAC system includes exhaust fans installed on the roof and throughout the building. | 1990 | 25 | 2015 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 2808.19 | 1.3 | 1.25 | 1 | 9126.62 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 61 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2000 | 35 | 2035 | 2035 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 350 | SF | 20.89 | 1.3 | 1.25 | 1 | 11881.19 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 72 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2009 | 35 | 2044 | 2044 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 350 | SF | 20.89 | 1.3 | 1.25 | 1 | 11881.19 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 107 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with exit signs showing to indicate the direction to the means of egress and includes single and double sided LED exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2010 | 35 | 2045 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 350 | SF | 20.89 | 1.3 | 1.25 | 1 | 11881.19 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 21 | Exterior Automatic Openers - Single | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2010 | 15 | 2025 | 2025 | 2019-10-15 | 2 - Good | The automatic door openers are functioning as intended; no significant deficiencies were observed. | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 31 | Exterior Automatic Openers - Single | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2010 | 15 | 2025 | 2025 | 2019-10-15 | 2 - Good | The automatic door openers are in good condition and functioning as intended. | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 50 | Exterior Automatic Openers - Single | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2010 | 15 | 2025 | 2026 | 2019-10-15 | 2 - Good | The automatic door openers are in good condition and functioning as intended. Lifecycle replacement can be deferred. | 1 | Each | 3743.74 | 1.3 | 1.25 | 1 | 6083.58 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 108 | Exterior Automatic Openers - Single | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2007 | 15 | 2022 | 2025 | 2019-10-15 | 2 - Good | The exterior door openers are in good condition overall, no deficiencies were observed or reported. Lifecycle replacement can be deferred. | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 22 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior - Single Door - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 30 | 2002 | 2026 | 2019-10-15 | 2 - Good | The interior doors are in fair condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 2 | Each | 2995.3 | 1.3 | 1.25 | 1 | 9734.73 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 90 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior - Single Door - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1982 | 30 | 2012 | 2021 | 2019-10-15 | 4 - Poor | The exterior door is in poor condition overall, lifecycle replacement is recommended. | 1 | Each | 2995.3 | 1.3 | 1.25 | 1 | 4867.36 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 10 | Exterior Lights | D502021 | Interior Lighting (Residential) | The exterior lighting includes wall mounted LED fixtures. | 2012 | 35 | 2047 | 2032 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 2500 | SF | 2.65 | 1.3 | 1.25 | 1 | 10765.63 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 74 | Exterior Soffits | B201008 | Exterior Soffits | The building includes prefinished metal soffits located at the loading dock. | 1972 | 50 | 2022 | 2026 | 2019-10-15 | 2 - Good | The soffits are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 527 | SF | 9.59 | 1.3 | 1.25 | 1 | 8212.64 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 89 | Exterior Stairs - Concrete | C201002 | Exterior (Attached) Stair Construction | The building includes cast in place stairs located at the loading dock area. | 1972 | 40 | 2012 | 2026 | 2019-10-15 | 2 - Good | The concrete stairs are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 2 | Per Riser | 936.32 | 1.3 | 1.25 | 1 | 3043.04 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 39 | Exterior Storefront Door - Single Leaf | B203005 | Exterior - Hangar Doors | The exterior doors of hollow metal glazed single - door mounted by butt hinges to metal door frame. | 2005 | 25 | 2030 | 2026 | 2019-10-15 | 2 - Good | The exterior door is in good condition overall, lifecycle replacement can be deferred. | 1 | Lump Sum | 7700 | 1.3 | 1.25 | 1 | 12512.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 128 | Faraday cage windows | C101005 | Interior Windows | The building&rsquo;s interior windows include faraday cage windows located in room 614. | 2007 | 75 | 2082 | 2057 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed or reported. | 54 | SF | 52.22 | 1.3 | 1.25 | 1 | 4582.31 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 919 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | New System | 2025 | 20 | 2045 | 2045 |  | 1 - Excellent |  | 1108 | SF Building | 4.58 | 1.3 | 1.25 | 1 | 8246.29 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 20 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | The building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 1998 | 25 | 2023 | 2028 | 2019-10-15 | 2 - Good | The casework is in good condition overall, no significant deficiencies were observed or reported. | 49 | LF | 171.33 | 1.3 | 1.25 | 1 | 13642.15 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 30 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | The building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2000 | 25 | 2025 | 2030 | 2019-10-15 | 1 - Excellent | The mill work is in good condition overall, no significant deficiencies were observed. | 39 | LF | 171.33 | 1.3 | 1.25 | 1 | 10858.04 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 38 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2000 | 25 | 2025 | 2030 | 2019-10-15 | 1 - Excellent | The millwork is in good condition overall, | 20 | LF | 171.33 | 1.3 | 1.25 | 1 | 5568.23 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 62 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2005 | 25 | 2030 | 2035 | 2019-10-15 | 1 - Excellent | The millwork is in good condition overall. | 33 | LF | 171.33 | 1.3 | 1.25 | 1 | 9187.57 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 73 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2009 | 25 | 2034 | 2039 | 2019-10-15 | 1 - Excellent | The system is in good condition overall, no significant deficiencies were observed or reported. | 20 | LF | 171.33 | 1.3 | 1.25 | 1 | 5568.23 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 87 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2005 | 25 | 2030 | 2035 | 2019-10-15 | 1 - Excellent | The mill work is in good condition overall, no significant deficiencies were observed. | 26 | LF | 171.33 | 1.3 | 1.25 | 1 | 7238.69 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 88 | Fixed Casework - Lab Benches | C103011 | Millwork General | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1972 | 25 | 1997 | 2021 | 2019-10-15 | 4 - Poor | The casework is in poor condition overall, lifecycle replacement is recommended. | 1023 | SF Building | 5.22 | 1.3 | 1.25 | 1 | 8677.6 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 3 | Gas-Tight Vault Doors | C102099 | Other Interior Doors | The building includes gas tight vault type doors in steel frames located at the CL3 lab at room 568. | 2012 | 40 | 2052 | 2052 | 2019-10-15 | 1 - Excellent | The doors are in good condition overall, no major deficiencies were observed. | 2 | Lump Sum | 3850 | 1.3 | 1.25 | 1 | 12512.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 55 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 15 | 1987 | 2026 | 2019-10-15 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 3122 | SF | 2.65 | 1.3 | 1.25 | 1 | 13444.11 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 78 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include GWB ceiling located in the corridors. | 1972 | 15 | 1987 | 2026 | 2019-10-15 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 2791 | SF | 2.65 | 1.3 | 1.25 | 1 | 12018.74 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 121 | Hand-wash Sinks | D201004 | Sinks | The plumbing fixtures include stainless steel and porcelain hand-wash sinks. | 1972 | 35 | 2007 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 977.9 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 116 | Handwash & Kitchen Sinks | D201004 | Sinks | The plumbing fixtures include stainless steel handwash and kitchen sinks. | 1972 | 35 | 2007 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 977.9 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 112 | Heat Exchanger - Liquid/Liquid - Plate and Frame | D302011 | Steam Boilers - Over 1000 MBH | The HVAC system includes plate and frame, liquid to liquid, heat exchangers providing heated glycol for the snow melt system near the main entrance. | 2007 | 30 | 2037 | 2037 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 500 | MBH | 56.21 | 1.3 | 1.25 | 1 | 45670.63 | 1 | Active |  |  |  |  | Academic | Central
Planning | 04.758 | 1 | Humanities Fine Arts | Morris | 9 | Heat Exchangers | D302011 | Steam Boilers - Over 1000 MBH | The HVAC system is provided with plate & frame heat exchangers. | 2012 | 30 | 2042 | 2031 | 2019-10-15 | 3 - Fair | Repair good shape | 2700 | MBH | 56.21 | 1.3 | 1.25 | 1.49 | 367465.85 | 2 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 17 | Humidity Control Equipment - Steam Humidification | D304061 | Fuel-Fired Humidifiers | The HVAC system is equipped with a steam humidification system which supply humidification to the Trane air handler. | 1998 | 20 | 2018 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 4679.29 | 1.3 | 1.25 | 1 | 7603.85 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 85 | Humidity Control Equipment - Steam Humidification | D304061 | Fuel-Fired Humidifiers | The HVAC system is equipped with a NORTEC steam humidification unit for AHU-1. | 1997 | 20 | 2017 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 4679.29 | 1.3 | 1.25 | 1 | 7603.85 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 105 | Humidity Control Equipment - Steam Humidification | D304061 | Fuel-Fired Humidifiers | The HVAC system is equipped with a NORTEC steam humidification unit which supplys humidification to the main 2,0000 CFM air handler. | 1998 | 20 | 2018 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 4679.29 | 1.3 | 1.25 | 1 | 7603.85 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 32 | Interior Automatic Openers - Single | C102007 | Interior - Automatic Door Openers | The building includes automatic openers for single swing doors. | 2010 | 15 | 2025 | 2025 | 2019-10-15 | 2 - Good | The automatic door openers are functioning as intended, no deficiencies were observed. | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 75 | Interior Automatic Openers - Single | C102007 | Interior - Automatic Door Openers | The building includes interior doors with automatic openers for single swing doors located in 300 floor corridor. | 2005 | 15 | 2020 | 2030 | 2019-10-15 | 3 - Fair | The door openers are functioning as intended, life cycle replacement can be deferred. Repaired lower panel in 2025 | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 2 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 97 | Interior Automatic Openers - Single | C102007 | Interior - Automatic Door Openers | The building includes automatic openers for single swing doors. | 1994 | 15 | 2009 | 2025 | 2019-10-15 | 2 - Good | The automatic door openers are functioning as intended, no deficiencies were observed. Lifecycle replacement can be deferred. | 1 | Each | 3743.74 | 1.3 | 1.25 | 1 | 6083.58 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 11 | Interior Metal Gate | C101028 | Interior Guardrails and Screens | The building's interior doors include a wrought iron gate located in the 100 floor level wine cellar. | 1998 | 50 | 2048 | 2048 | 2019-10-15 | 1 - Excellent | The iron gate is in good condition overall and functioning as intended. | 10 | LF | 285.39 | 1.3 | 1.25 | 1 | 4637.59 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 33 | Interior Stairs - Cast-In-Place Concrete | C201001 | Interior Stair Construction | The building includes cast-in-place concrete stairs that provide access to different levels of the building. | 1972 | 75 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | The stairs are in fair condition overall, no significant deficiencies were observed or reported. | 120 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 146095.95 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 23 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes cast in place concrete stairs that provides access to different levels in the building. | 1972 | 75 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 160 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 194794.6 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 51 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes Cast-in-place concrete stairs that provide access to different levels of the building. | 1972 | 75 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 40 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 48698.65 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 63 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes Cast-in-place concrete stairs that provide access to different levels of the building. | 1972 | 75 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 40 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 48698.65 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 76 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes cast in place concrete stairs that provides access to different levels in the building. | 1972 | 75 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | The stairs are in good condition overall, no significant deficiencies were observed. | 100 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 121746.63 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 91 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes cast in place concrete stairs that provides access to different levels in the building. | 1982 | 75 | 2057 | 2057 | 2019-10-15 | 1 - Excellent | The cast in place concrete stairs are in good condition overall, no deficiencies were observed. | 80 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 97397.3 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 98 | Interior Stairs - Cast-In-Place Concrete Treads | C201001 | Interior Stair Construction | The building includes Cast-in-place concrete stairs that provide access to different levels of the building. | 1994 | 75 | 2069 | 2069 | 2019-10-15 | 1 - Excellent | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 120 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 146095.95 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 40 | Interior Stairs - Cast-In-Place Concrete Treads - 22 Risers | C201001 | Interior Stair Construction | The building includes cast-in-place concrete stairs that provide access to different levels of the building. | 1972 | 75 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | The stairs are in good condition overall, no significant deficiencies were observed or reported. | 120 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 146095.95 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 12 | Interior Stairs - Concrete Filled Metal Pan Treads | C201001 | Interior Stair Construction | The building's interior stairs are concrete filled metal pan stairs with ceramic tile finish. | 1998 | 75 | 2073 | 2073 | 2019-10-15 | 1 - Excellent | The interior stairs are in good condition overall, no deficiencies were observed. | 60 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 73047.98 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 41 | Interior Stairs - Concrete Filled Metal Pan Treads | C201001 | Interior Stair Construction | The building includes concrete filled metal pan stairs. | 2005 | 75 | 2080 | 2072 | 2019-10-15 | 1 - Excellent | The stairs are in good condition overall, no significant deficiencies were observed. | 40 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 48698.65 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 109 | Interior Stairs - Concrete Filled Metal Pan Treads | C201001 | Interior Stair Construction | Access to the upper levels is via concrete filled metal pan stairs. | 2007 | 75 | 2082 | 2082 | 2019-10-15 | 1 - Excellent | The interior stairs are in good condition overall. | 200 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 243493.25 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 6 | Interior Stairs - Concrete Finish | C201001 | Interior Stair Construction | The building includes two sets of cast-in-place concrete stairs with sealed concrete finish and metal railings. | 2012 | 75 | 2087 | 2087 | 2019-10-15 | 1 - Excellent | The interior stairs are in good condition overall, no major deficiencies were observed. | 120 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 146095.95 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 52 | Interior Stairs - Steel Plate Treads - Air Plenum 100 Floor Level | C201001 | Interior Stair Construction | The building includes a steel plate stairs with 12 risers per flight located in the 100 floor. The stairs are not accessible by the public. | 1972 | 75 | 2047 | 2047 | 2019-10-15 | 1 - Excellent | The stairs are in good condition overall, no significant deficiencies were observed. | 25 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 30436.66 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 5 | Interior Stairs - Tiled | C201001 | Interior Stair Construction | The building includes three sets of cast-in-place concrete stairs with slate tile risers and landings and metal, glass, and plastic railings. | 2012 | 75 | 2087 | 2022 | 2019-10-15 | 3 - Fair | The slate tiles are starting to deteriorate at the main stairs due to the excessive amount of traffic and it is acting as a tripping hazard. Replacement of the slate tiles are recommended. | 240 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 292191.9 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 120 | IT Room Fire Suppression | D409005 | Dry Chemical Fire Extinguishing Systems (Kitchen Hood) | The IT Server room is provided with a Pyro-Chem FM-200 fire suppression system. | 2015 | 20 | 2035 | 2035 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 3911.6 | 1.3 | 1.25 | 1 | 6356.35 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 111 | Kitchen Sinks | D201004 | Sinks | The plumbing fixtures include kitchen sinks located in the break rooms. | 2007 | 35 | 2042 | 2042 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 977.9 | 1.3 | 1.25 | 1 | 4767.26 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 14 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sinks serving the break rooms. | 2009 | 35 | 2044 | 2044 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 4 | Each | 977.9 | 1.3 | 1.25 | 1 | 6356.35 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 25 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single and double bowl kitchen sinks in the staff rooms and medical rooms on the first and second floors. | 2003 | 35 | 2038 | 2038 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 5 | Each | 977.9 | 1.3 | 1.25 | 1 | 7945.44 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 35 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sinks in the staff rooms on the first and second floors. | 1995 | 35 | 2030 | 2030 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 977.9 | 1.3 | 1.25 | 1 | 4767.26 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 58 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sinks in the break rooms. | 2000 | 35 | 2035 | 2035 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 977.9 | 1.3 | 1.25 | 1 | 4767.26 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 65 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sinks serving the break rooms. | 2009 | 35 | 2044 | 2044 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 977.9 | 1.3 | 1.25 | 1 | 4767.26 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 81 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl kitchen sink located in the break rooms. | 2010 | 35 | 2045 | 2045 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 6 | Each | 977.9 | 1.3 | 1.25 | 1 | 9534.53 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 102 | Kitchenette Sinks | D201004 | Sinks | The plumbing fixtures include single bowl stainless steel kitchen sinks in the break rooms. | 2000 | 35 | 2035 | 2035 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 977.9 | 1.3 | 1.25 | 1 | 3178.18 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 66 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 6 | Each | 977.9 | 1.3 | 1.25 | 1 | 9534.53 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 80 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. Note that the labs are no longer used as lab sinks. | 2000 | 35 | 2035 | 2035 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 4 | Each | 977.9 | 1.3 | 1.25 | 1 | 6356.35 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 60 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system consists of recessed mounted fixtures around the perimeter of the building. | 2000 | 35 | 2035 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1500 | SF | 2.65 | 1.3 | 1.25 | 1 | 6459.38 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 71 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system consists of surface and recessed mounted fixtures, conduit and wire. | 2000 | 35 | 2035 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2000 | SF | 2.65 | 1.3 | 1.25 | 1 | 8612.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 898 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system generally includes recessed and surface mounted fixtures, conduit, wire and breakers. | 2025 | 35 | 2060 | 2057 |  | 2 - Good |  | 2500 | SF | 2.65 | 1.3 | 1.25 | 1 | 10765.63 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 904 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system includes wall mounted LED units around the perimeter of the building. | 2026 | 35 | 2061 | 2056 |  | 2 - Good |  | 3000 | SF | 2.65 | 1.3 | 1.25 | 1 | 12918.75 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 2 | Metal Panel Soffits and canopy | B201008 | Exterior Soffits | The building includes metal panel soffits and canopy located at the main entrance | 2010 | 50 | 2060 | 2027 | 2019-10-15 | 4 - Poor | The system is in good condition overall, no deficiencies were observed or reported. | 285 | SF | 9.59 | 1.3 | 1.25 | 1 | 4441.37 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 129 | Metal panels | C301099 | Other Wall Finishes | The building&rsquo;s interior finishes include insulated metal panel walls located in the 5th floor mechanical room. | 2007 | 30 | 2037 | 2037 | 2019-10-15 | 1 - Excellent | The metal panel wall finish in good condition overall, no major deficiencies were observed. | 2 | Lump Sum | 3850 | 1.3 | 1.25 | 1 | 12512.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 1 | Overhead Doors | B203008 | Exterior - Automatic Door Openers | At the drive-in bay metal insulated segmented overhead doors are provided.The overhead doors are automatically operated. | 2000 | 15 | 2015 | 2030 | 2019-10-15 | 4 - Poor | No major deficiencies were observed or reported. | 3 | Each | 3743.74 | 1.3 | 1.25 | 1 | 18250.73 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 34 | Painted Floor Finish | C302007 | Painted / Sealed Floor | The building's floor finishes include painted floor finish located at 500 floor storage room and electrical rooms. | 2010 | 15 | 2025 | 2026 | 2019-10-15 | 2 - Good | The painted floor finish is in good condition overall, lifecycle replacement can be deferred. | 852 | SF | 3.65 | 1.3 | 1.25 | 1 | 5053.43 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 99 | Painted Floor Finish | C302007 | Painted / Sealed Floor | The building's floor finishes include painted floor finish located at storage rooms and electrical rooms. | 2010 | 15 | 2025 | 2025 | 2019-10-15 | 2 - Good | The painted floor finish is in good condition overall. | 1000 | SF | 3.65 | 1.3 | 1.25 | 1 | 5931.25 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 114 | Painted/ Sealed floors | C302007 | Painted / Sealed Floor | The building includes painted / sealed concrete floors located in the mechanical rooms | 1972 | 15 | 1987 | 2022 | 2019-10-15 | 3 - Fair | The painted floor finish has aged and is in poor condition, lifecycle replacement is recommended | 344 | SF | 3.65 | 1.3 | 1.25 | 1 | 2040.35 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 130 | Polished concrete | C302099 | Other Floor Finishes | Majority of the building&rsquo;s floor is finished with polished concrete. | 2007 | 20 | 2027 | 2027 | 2019-10-15 | 2 - Good | The polished concrete floor finish is in good condition overall, no major deficiencies were observed. | 1 | Lump Sum | 3850 | 1.3 | 1.25 | 1 | 6256.25 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 127 | Roof access stairs | C201001 | Interior Stair Construction | The building&rsquo;s interior stairs include metal framed stairs that provide access to the roof. | 2007 | 75 | 2082 | 2082 | 2019-10-15 | 1 - Excellent | The interior stairs are in good condition overall, no major deficiencies were observed. | 25 | Per Riser | 749.21 | 1.3 | 1.25 | 1 | 30436.66 | 0 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 44 | Rooftop Unit - SF-1 | D304011 | Refrigerant Distribution Systems | Cooling and heating for select areas is provided from a YORK, 400,000 BTU, gas fired, rooftop unit with electric cooling. | 2008 | 45 | 2053 | 2038 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 14500 | SF | 4.36 | 1.3 | 1.25 | 1 | 102732.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 45 | Rooftop Unit - SF-3 | D304011 | Refrigerant Distribution Systems | Cooling and heating for select areas is provided from a YORK, 138,000 BTU, gas fired, rooftop unit with electric cooling. | 2008 | 45 | 2053 | 2038 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 14500 | SF | 4.36 | 1.3 | 1.25 | 1 | 102732.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 46 | Rooftop Unit - SF-4 | D304011 | Refrigerant Distribution Systems | Cooling and heating for select areas is provided from a YORK, gas fired, rooftop unit. | 2008 | 45 | 2053 | 2038 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 14500 | SF | 4.36 | 1.3 | 1.25 | 1 | 102732.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 119 | Science stores A/C | D305041 | Heat Pumps | The Science stores is provided with a heat pump. | 2011 | 18 | 2029 | 2029 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 5378.45 | 1.3 | 1.25 | 1 | 8739.98 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 77 | Sealed concrete floor finish | C302007 | Painted / Sealed Floor | The building's floor finish include sealed concrete floor located in the loading dock. | 1972 | 15 | 1987 | 1987 | 2019-10-15 | 5 - Critical | The sealed concrete finish is in poor condition, lifecycle replacement is recommended. | 2002 | SF | 3.65 | 1.3 | 1.25 | 1 | 11874.36 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 47 | Split DX Ductless Unit - 1.5 Tons | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for the rock storage room is provided from an LG, 1.5 ton, split DX, condensing unit. | 2008 | 18 | 2026 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 3743.74 | 1.3 | 1.25 | 1.5 | 9125.37 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 48 | Split DX Ductless Unit - 2 Tons | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for the rock storage room is provided from a CARRIER, 2 ton, split DX, condensing unit. | 2008 | 18 | 2026 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 3743.74 | 1.3 | 1.25 | 1 | 12167.16 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 4 | Stainless Steel Doors | C102021 | Interior - Single Door - Hollow Metal | Stainless steel doors with stainless steel frames are provided at the MCC bridge. | 2012 | 40 | 2052 | 2052 | 2019-10-15 | 1 - Excellent | The doors are in good condition and are functioning as intended. | 2 | Each | 2340.03 | 1.3 | 1.25 | 1 | 7605.1 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 123 | Steel framed guardrails | B201007 | Exterior Guards and Railings | The building includes steel framed guardrails located on the 300 floor | 1982 | 25 | 2007 | 2026 | 2019-10-15 | 2 - Good | The guardrails are in fair condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 26 | LF | 298.06 | 1.3 | 1.25 | 1 | 12593.04 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 101 | Stucco ceiling | C303006 | Painted Ceiling Structures | The ceiling located on the J430 floor level includes a latex painted ceiling finishes on concrete deck substrate. | 1994 | 15 | 2009 | 2025 | 2019-10-15 | 2 - Good | The ceiling finish is in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 1292 | SF | 2.65 | 1.3 | 1.25 | 1 | 5563.68 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 42 | Sump Pump - Submersible - 1/2 HP | D203006 | Sanitary Waste Ejector Pump Systems | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 15 | 2012 | 2047 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 4889.5 | 1.3 | 1.25 | 1 | 7945.44 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 56 | Sump Pump - Submersible - 1/2 HP | D203006 | Sanitary Waste Ejector Pump Systems | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 15 | 2012 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 4889.5 | 1.3 | 1.25 | 1 | 7945.44 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 54 | Terrazzo Flooring - Cast In Place | C302002 | Terrazzo Floor | The building's floor finish includes terrazzo floor finish. | 1972 | 50 | 2022 | 2026 | 2019-10-15 | 2 - Good | The floor finish is in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 183 | SF | 39.13 | 1.3 | 1.25 | 1 | 11636.28 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 86 | Unit Heaters | D305002 | Unit Heaters (Hydronic) | Heating for the loading dock and Main Electrical Vault is provided by suspended, electric, unit heaters. | 1997 | 30 | 2027 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 2933.7 | 1.3 | 1.25 | 1 | 14301.79 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 49 | Unit Heaters - Electric | D305002 | Unit Heaters (Hydronic) | Heating for the rock storage area is provided by a suspended, electric, unit heater. | 1997 | 30 | 2027 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 2933.7 | 1.3 | 1.25 | 1 | 4767.26 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 96 | Unit Heaters - Electric | D305002 | Unit Heaters (Hydronic) | Heating for the boiler room and the Main Electrical Vault is each provided by a suspended electric unit heater. | 1990 | 30 | 2020 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 2933.7 | 1.3 | 1.25 | 1 | 9534.53 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 70 | Unit Heaters - Electric (Each) | D305002 | Unit Heaters (Hydronic) | Heating for the rock storage area is provided by a suspended, electric, unit heater. | 1985 | 30 | 2015 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 2933.7 | 1.3 | 1.25 | 1 | 4767.26 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 106 | Unit Heaters - Hot Water | D305002 | Unit Heaters (Hydronic) | Space heating in mechanical roooms is provided by suspended, forced hot water unit heaters. | 1994 | 30 | 2024 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 2933.7 | 1.3 | 1.25 | 1 | 9534.53 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 124 | Vinyl tile | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include vinyl tiles located in room J201 | 2016 | 15 | 2031 | 2031 | 2019-10-15 | 1 - Excellent | The vinyl tiles are in good condition overall, no significant deficiencies were observed. | 1076 | SF | 9.08 | 1.3 | 1.25 | 1 | 15876.38 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 118 | Walk-in Coolers and Freezers | E109002 | Basketball Backboards - Fixed | The building is provided with walk-in coolers and freezers. | 1997 | 30 | 2027 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 4679.29 | 1.3 | 1.25 | 1 | 15207.69 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 24 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 2000 | 30 | 2030 | 2030 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. Replacement can be deferred. | 5 | Each | 1404.48 | 1.3 | 1.25 | 1 | 11411.4 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 36 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1990 | 30 | 2020 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 1404.48 | 1.3 | 1.25 | 1 | 6846.84 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 43 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1995 | 30 | 2025 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 1404.48 | 1.3 | 1.25 | 1 | 6846.84 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 59 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 1990 | 30 | 2020 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 1404.48 | 1.3 | 1.25 | 1 | 6846.84 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 67 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers on each floor. | 1990 | 30 | 2020 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 1404.48 | 1.3 | 1.25 | 1 | 9129.12 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 103 | Water Coolers | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 2000 | 30 | 2030 | 2025 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 1404.48 | 1.3 | 1.25 | 1 | 6846.84 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 122 | Water Fountains | D201006 | Drinking Water Fountains (Non-refrigerated) | The plumbing fixtures includes stainless steel water fountains. | 1982 | 30 | 2012 | 2026 | 2019-10-15 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 6 | Each | 1466.85 | 1.3 | 1.25 | 1 | 14301.79 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 113 | Water Treatment System | D202023 | Domestic Water Conditioners - Other | The water for the Boilers are provided from a CULLIGAN water treatment system. | 2012 | 20 | 2032 | 2032 | 2019-10-15 | 1 - Excellent | No significant deficiencies were observed. | 1 | Lump Sum | 7700 | 1.3 | 1.25 | 1 | 12512.5 | 1 | Active |  |  |  |  | Academic | Central
| 04.758 | 1 | Humanities Fine Arts | Morris | 115 | Wood laminate flooring | C302003 | Hardwood Floor | The building's floor finishes include wood laminate flooring located in room C301. | 2015 | 30 | 2045 | 2035 | 2019-10-15 | 1 - Excellent | The floor is in good condition overall. | 323 | SF | 21.75 | 1.3 | 1.25 | 1 | 11416.03 | 1 | Active |  |  |  |  | Academic | Central
| 03.523 | 2 | Kirby Student Ctr | Duluth | 168 | Acoustic Tile Ceiling - Exposed T-bar - 1972 | C303007 | Suspended Acoustic Ceiling Panels | The building includes suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids located 300 floor. | 1972 | 25 | 1997 | 2028 | 2019-11-07 | 4 - Poor | The ceiling tiles are in poor condition overall, lifecycle replacement is recommended. | 1378 | SF | 7.87 | 1.3 | 1.05 | 1 | 14803.23 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 144 | Air Compressors | D306004 | Air Compressors and Dryers (Building Controls) | Lab air compressors consists of two 25HP, ATLAS COPCO, oil-less, rotary tooth, compressors with a 660 gallon receiver and two 106SCFM desiccant air dryers. | 2012 | 15 | 2027 | 2037 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 6551.16 | 1.3 | 1.05 | 1 | 17884.67 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 142 | Aluminum Panel Cladding | B201028 | Insulated Metal Sandwich Panels | The building&rsquo;s exterior finishes include aluminum panel cladding located at the stairwells above the roof. | 2012 | 40 | 2052 | 2052 | 2019-11-07 | 1 - Excellent | The aluminum cladding exterior wall finish is in good condition overall, no deficiencies were observed. | 301 | SF | 30.4 | 1.3 | 1.05 | 1 | 12490.3 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 197 | B301023 - Conventional - Single Ply Membrane | B301023 | Conventional - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2022 | 20 | 2042 | 2042 | 2019-11-07 | 1 - Excellent |  | 250 | SF | 16.1 | 1.3 | 1.05 | 1.5 | 8241.19 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 901 | B301023 - Conventional - Single Ply Membrane | B301023 | Conventional - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2023 | 20 | 2043 | 2042 |  | 1 - Excellent |  | 253 | SF | 16.1 | 1.3 | 1.05 | 1.5 | 8340.08 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 198 | B301027 - Asphalt Shingle | B301027 | Asphalt Shingle | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2023 | 15 | 2038 | 2038 | 2019-11-07 | 1 - Excellent |  | 1950 | SF | 5.22 | 1.3 | 1.05 | 1 | 13894.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 200 | C302002 - Terrazzo | C302002 | Terrazzo Floor | The building&rsquo;s floor finishes include carpet tile floor finish located in the offices | 2023 | 50 | 2073 | 2073 | 2019-11-07 | 1 - Excellent |  | 425 | SF | 39.13 | 1.3 | 1.05 | 1 | 22700.29 | 0 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 920 | C302003 - Hardwood Floor | C302003 | Hardwood Floor | The building's floor finishes include carpet tiles located in the offices. | 2025 | 30 | 2055 | 2055 |  | 2 - Good |  | 861 | SF | 21.75 | 1.3 | 1.05 | 1 | 25562.01 | 0 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 158 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet floor tiles located in the 200 floor. | 2005 | 10 | 2015 | 2026 | 2019-11-07 | 2 - Good | The carpet tiles are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 1830 | SF | 7.87 | 1.3 | 1.05 | 1 | 19658.87 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 186 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the offices. | 2014 | 10 | 2024 | 2025 | 2019-11-07 | 2 - Good | The carpet tiles are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 861 | SF | 7.87 | 1.3 | 1.05 | 1 | 9249.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 190 | Custodial/Utility Sinks | D201016 | Custodial Sinks | The plumbing fixtures include custodial/utility sinks in the janitor's closet on every other floor. | 2007 | 30 | 2037 | 2032 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 5 | Each | 1955.8 | 1.3 | 1.05 | 1 | 13348.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 178 | Distribution Equipment - Motor Control Centre | D501024 | Main Service Panels | The electrical distribution system for the building includes a motor control centre for the supply and control of electrical power to HVAC equipment and other motor loads. | 1985 | 40 | 2025 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 12166.77 | 1.3 | 1.05 | 1 | 16607.64 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 172 | Distribution Equipment - Motor Control Centres | D501024 | Main Service Panels | The electrical distribution system for the building includes motor control centres for the supply and control of electrical power to HVAC equipment and other motor loads. | 1972 | 40 | 2012 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 12166.77 | 1.3 | 1.05 | 1 | 16607.64 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 170 | Domestic Water Distribution - Backflow Preventer - 2012 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes two 4 inch backflow preventer installed in 2012, one on each of the two parallel lines. | 2012 | 40 | 2052 | 2052 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 2691 | SF Building | 3.65 | 1.3 | 1.05 | 1 | 13407.23 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 159 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 25 | 1997 | 2026 | 2019-11-07 | 2 - Good | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 1991 | SF | 7.87 | 1.3 | 1.05 | 1 | 21388.42 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 173 | Emergency Battery Pack Lights | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights. | 2000 | 20 | 2020 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SF Building | 0.5 | 1.3 | 1.05 | 1 | 19012.4 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 145 | Epoxy Flooring | C302007 | Painted / Sealed Floor | The building's floor finishes include cement epoxy floor finish located in rooms 216A and 306. | 1998 | 15 | 2013 | 2025 | 2019-11-07 | 2 - Good | The cement epoxy floor is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 4521 | SF | 3.65 | 1.3 | 1.05 | 1 | 22524.75 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 162 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The HVAC system includes centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1997 | 25 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 2808.19 | 1.3 | 1.05 | 1 | 15332.72 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 149 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with Exit Signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2000 | 35 | 2035 | 2035 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 500 | SF | 20.89 | 1.3 | 1.05 | 1 | 14257.43 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 180 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2010 | 35 | 2045 | 2045 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 600 | SF | 20.89 | 1.3 | 1.05 | 1 | 17108.91 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 146 | Exterior Concrete Accessible Ramp | B101002 | Reinforced Concrete Floor | The entrance includes a handicap accessible concrete ramp rails on both sides. | 2018 | 75 | 2093 | 2075 | 2019-11-07 | 1 - Excellent | The exterior ramp is in good condition overall, no deficiencies were observed. | 124 | SF Footprint | 77.04 | 1.3 | 1.05 | 1 | 13039.79 | 0 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 143 | Exterior Doors - Hollow Metal Doors | B203023 | Exterior - Single Door - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 2012 | 30 | 2042 | 2037 | 2019-11-07 | 1 - Excellent | No major deficiencies were observed or reported. | 4 | Each | 2995.3 | 1.3 | 1.05 | 1 | 16354.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 151 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior - Single Door - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 30 | 2002 | 2028 | 2019-11-07 | 2 - Good | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 4 | Each | 2995.3 | 1.3 | 1.05 | 1 | 16354.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 174 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior - Single Door - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 30 | 2002 | 2028 | 2019-11-07 | 3 - Fair | The doors have aged and are in poor condition, lifecycle replacement is recommended. | 4 | Each | 2995.3 | 1.3 | 1.05 | 1 | 16354.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 175 | Exterior Overhead Sectional Doors | B203008 | Exterior - Automatic Door Openers | The building includes rolling overhead doors located at the loading dock. The doors are automatically operated. | 2000 | 15 | 2015 | 2031 | 2019-11-07 | 2 - Good | The doors are in good condition overall, no significant deficiencies were observed. Repairs done in 2025, life extended 5 years | 3 | Each | 3743.74 | 1.3 | 1.05 | 1 | 15330.62 | 1 | Active | 636 |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 185 | Exterior Storefront Door - Double Leaf | B203028 | Exterior - Double Door - Aluminum and Glass | The exterior doors consist of aluminum framed glazed double -doors mounted by butt hinges to aluminum door frames. | 1994 | 35 | 2029 | 2026 | 2019-11-07 | 2 - Good | The exterior doors are in good condition overall, lifecycle replacement can be deferred. | 1 | Each | 8423.03 | 1.3 | 1.05 | 1 | 11497.44 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 187 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2014 | 25 | 2039 | 2044 | 2019-11-07 | 1 - Excellent | The millwork is in good condition overall, no significant deficiencies were observed. | 53 | LF | 171.33 | 1.3 | 1.05 | 1 | 12394.87 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 164 | Fixed Casework - Lab Benches | C103011 | Millwork General | The building includes metal lab benches with acid resistant countertops. | 1972 | 25 | 1997 | 2026 | 2019-11-07 | 2 - Good | The lab benches are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred | 1776 | SF Building | 5.22 | 1.3 | 1.05 | 1 | 12654.53 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 184 | Foundation Wall and Footings | A101002 | Low Rise - 1 - 3 Level Building Foundation | The building is a two -storey structure without a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1994 | 75 | 2069 | 2069 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed or reported. | 7092 | SF Footprint | 23.11 | 1.3 | 1.05 | 1 | 223718.2 | 0 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 165 | Foundation Wall and Footings - 12-ft. - Full Basement | A202002 | Basement Walls | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1972 | 75 | 2047 | 2035 | 2019-11-07 | 1 - Excellent | Repairs completed | 1400 | SF Footprint | 34.69 | 1.3 | 1.05 | 1 | 66292.59 | 3 | Active | 544 |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 194 | Glazed partitions | C101006 | Glazed Partitions | The building includes window units and storefront windows installed in partition openings located on the 300 floor level. | 1982 | 75 | 2057 | 2032 | 2019-11-07 | 1 - Excellent | The glazed partitions are in fair condition overall, no significant deficiencies were observed | 226 | SF | 65.24 | 1.3 | 1.05 | 1 | 20125.89 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 148 | Interior Automatic Openers - Single | C102007 | Interior - Automatic Door Openers | The building includes interior doors with automatic openers for single swing doors located in 400 floor office area. | 2005 | 15 | 2020 | 2026 | 2019-11-07 | 2 - Good | The door openers are functioning as intended, lifecycle replacement can be deferred. | 3 | Each | 3743.74 | 1.3 | 1.05 | 1 | 15330.62 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 152 | Interior Automatic Openers - Single | C102007 | Interior - Automatic Door Openers | The building includes automatic openers for single swing doors. | 2010 | 15 | 2025 | 2025 | 2019-11-07 | 2 - Good | The automatic door openers are functioning as intended, no deficiencies were observed. | 3 | Each | 3743.74 | 1.3 | 1.05 | 1 | 15330.62 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 156 | Interior Coiling Counter Doors - 6' x 4' | C102006 | Interior - Overhead Doors - Industrial | The building includes coiling counter doors located in room E304. | 2010 | 30 | 2040 | 2040 | 2019-11-07 | 1 - Excellent | The coiling doors are in good condition overall, no significant deficiencies were observed or reported. | 1 | Each | 11230.45 | 1.3 | 1.05 | 1 | 15329.56 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 188 | Interior Doors - Special | C102099 | Other Interior Doors | The interior doors located on the 600 floor level include copper shielded doors. | 2007 | 40 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | The copper shielded doors are functioning as intended. | 3 | Lump Sum | 3850 | 1.3 | 1.05 | 1 | 15765.75 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 176 | Interior Overhead Rolling Doors - 10' x 10' | C102006 | Interior - Overhead Doors - Industrial | The building includes a sectional overhead door that is automatically operated located in the 200 floor kitchen. | 1972 | 30 | 2002 | 2026 | 2019-11-07 | 2 - Good | The interior door is in good condition overall and functioning as intended. lifecycle replacement can be deferred. | 1 | Each | 11230.45 | 1.3 | 1.05 | 1 | 15329.56 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 195 | Interior Windows | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 300 floor. | 1994 | 75 | 2069 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Lifecycle replacement can be deferred. | 269 | SF | 52.22 | 1.3 | 1.05 | 1 | 19174.4 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 150 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 16 | Each | 977.9 | 1.3 | 1.05 | 1 | 21357.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 154 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 16 | Each | 977.9 | 1.3 | 1.05 | 1 | 21357.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 160 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2000 | 35 | 2035 | 2035 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 17 | Each | 977.9 | 1.3 | 1.05 | 1 | 22692.17 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 179 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting includes flush mounted fixtures around the perimeter of the building. | 2000 | 35 | 2035 | 2030 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 5000 | SF | 2.65 | 1.3 | 1.05 | 1 | 18086.25 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 183 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system consists of recessed mounted fixtures with CF lamps, conduit and wire. | 2000 | 35 | 2035 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 5000 | SF | 2.65 | 1.3 | 1.05 | 1 | 18086.25 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 191 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system includes surface mounted HID fixtures around the perimeter of the building. | 2007 | 35 | 2042 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 3500 | SF | 2.65 | 1.3 | 1.05 | 1 | 12660.38 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 199 | Section A | B301026 | Inverted - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2023 | 28 | 2051 | 2051 | 2019-11-07 | 1 - Excellent |  | 850 | SF | 18.74 | 1.3 | 1.05 | 1 | 21743.09 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 157 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1972 | 20 | 1992 | 2021 | 2019-11-07 | 4 - Poor | The wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 19267 | SF Building | 0.64 | 1.3 | 1.05 | 1 | 16831.65 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 166 | Single doors | C102024 | Interior - Double Door - Hollow Metal | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 1972 | 30 | 2002 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 2 | Each | 5615.61 | 1.3 | 1.05 | 1 | 15330.62 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 147 | Soffit - Plaster on Metal Lath | B201008 | Exterior Soffits | The buildings overhang soffit is a plaster-on-metal lath soffit. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed on the exposed soffits. Lifecycle replacment can be deferred. | 1292 | SF | 9.59 | 1.3 | 1.05 | 1 | 16912.73 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 155 | Split Condensing Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for the some of the offices is provided from a split condensing unit having a cooling capacity of 3 tons. | 2008 | 18 | 2026 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 3743.74 | 1.3 | 1.05 | 1 | 15330.62 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 169 | Sump Pump - Submersible - 1/2 HP | D203001 | Sanitary Waste and Vent Piping and Fittings | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 50 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 2691 | SF Building | 4.15 | 1.3 | 1.05 | 1 | 15243.84 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 189 | Sump Pump - Submersible - 1/2 HP | D203006 | Sanitary Waste Ejector Pump Systems | The water drainage system includes duplex sanitary sump pump systems. | 2007 | 15 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Lifecycle replacement can be deferred. | 2 | Each | 4889.5 | 1.3 | 1.05 | 1 | 13348.34 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 177 | Transformers - 15 KVA | D501026 | Grounding Methods | The building is equipped with a 15 KVA, 600V - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 9358.58 | 1.3 | 1.05 | 1 | 12774.46 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 163 | Transformers - 30 KVA | D501026 | Grounding Methods | The building is equipped with three 30KVA, 600V - 208Y/120V, 3-Phase, transformers. | 2008 | 50 | 2058 | 2048 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 9358.58 | 1.3 | 1.05 | 1 | 12774.46 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 182 | Transformers - 30 KVA & 15 KVA | D501026 | Grounding Methods | The electrical system is equipped with a 30 KVA, 600V - 208Y/120V transformer; and a 15 KVA, 600V - 208Y/120V transformer located in the Main Electrical Room. | 1982 | 50 | 2032 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 9358.58 | 1.3 | 1.05 | 1 | 12774.46 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 153 | Vinyl Tile Flooring - 2005 | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include VCT floor finish. | 1997 | 15 | 2012 | 2026 | 2019-11-07 | 2 - Good | The vinyl tiles are in good condition overall, lifecycle replacement can be deferred. | 1464 | SF | 9.08 | 1.3 | 1.05 | 1 | 18145.11 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 167 | Vinyl Tile Flooring - 2009 | C302022 | Vinyl Tile / Plank Floor | The building's floor finish includes vinyl tiles located in the 300 floor. | 2009 | 15 | 2024 | 2026 | 2019-11-07 | 2 - Good | The vinyl tiles are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 1615 | SF | 9.08 | 1.3 | 1.05 | 1 | 20016.63 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 192 | Walk-in Coolers and Freezers | E109002 | Basketball Backboards - Fixed | The building is provided with walk-in coolers and freezers. | 2007 | 30 | 2037 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 3 | Each | 4679.29 | 1.3 | 1.05 | 1 | 19161.69 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 193 | Walk-in Coolers and Freezers | E109002 | Basketball Backboards - Fixed | The building is provided with walk-in coolers and freezers. | 1972 | 30 | 2002 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 4679.29 | 1.3 | 1.05 | 1 | 19161.69 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 181 | Water Coolers - Wall Mounted (Each) | D201007 | Bidets | Plumbing fixtures include wall mounted stainless steel water coolers in the corridors. | 2000 | 30 | 2030 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 1404.48 | 1.3 | 1.05 | 1 | 15336.92 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 196 | Water Fountain - Wall Mounted | D201007 | Bidets | The building is provided with ELKAY EZH2O, wall-mounted, drinking fountains. | 2018 | 30 | 2048 | 2033 | 2019-11-07 | 1 - Excellent | No significant deficiencies were provided. | 8 | Each | 1404.48 | 1.3 | 1.05 | 1 | 15336.92 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 171 | Water Heater - 2013 - 142 L | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 142 litre, electric, SPACESAVER, water heater rated at 3000 W. | 2013 | 20 | 2033 | 2025 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 5615.61 | 1.3 | 1.05 | 1 | 7665.31 | 1 | Active |  |  |  |  | Operations | North
| 03.523 | 2 | Kirby Student Ctr | Duluth | 161 | Water Heater - Elec - Residential - 143 Litre | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a 143 litre, SPACESAVER, electric, water heater rated at 3000 W. | 2010 | 20 | 2030 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5615.61 | 1.3 | 1.05 | 1 | 15330.62 | 1 | Active |  |  |  |  | Operations | North
| 05.855 | 3 | Lysaker Gym | Crookston | 243 | Acoustic Tile Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | The building includes suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2005 | 25 | 2030 | 2025 | 2019-11-08 | 2 - Good | The ceiling tiles are in good condition overall, no significant deficiencies were observed. | 2260 | SF | 7.87 | 1.3 | 1.15 | 1 | 26590.37 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 238 | Acoustic Tile Ceiling - Exposed T-bar - 2009 | C303007 | Suspended Acoustic Ceiling Panels | The building includes suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids located 300 floor. | 2009 | 25 | 2034 | 2029 | 2019-11-08 | 2 - Good | The acoustic ceiling tiles are in good condition overall, no deficiencies were observed or reported. | 2325 | SF | 7.87 | 1.3 | 1.15 | 1 | 27355.14 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 204 | Acoustic Wall Panels | C301007 | Acoustic Wall Panels | Acoustic sound proof wall panels are provided in lecture room 219. | 2012 | 25 | 2037 | 2037 | 2019-11-08 | 1 - Excellent | The panels are in good condition overall, no deficiencies were observed. | 1184 | SF | 21.75 | 1.3 | 1.15 | 1 | 38499.24 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 201 | Aluminum Framed IGUs | B202001 | Windows | The building includes punched windows with aluminum frames and insulated glazing units in stone cladding. | 2012 | 35 | 2047 | 2042 | 2019-11-08 | 1 - Excellent | The windows are in good condition overall, no deficiencies were observed. | 175 | SF | 82.62 | 1.3 | 1.15 | 1 | 21615.46 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 211 | Autoclaves | E109099 | Other Equipment (Other) | The building is provided with six autoclaves in the CL3 lab with steam sterilizers. | 2012 | 25 | 2037 | 2032 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 6 | Lump Sum | 3850 | 1.3 | 1.15 | 1 | 34534.5 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 273 | Automatic door openers | B203008 | Exterior - Automatic Door Openers | Automatic door opening devices with door operators are provided at the building entrance vestibules. | 2000 | 15 | 2015 | 2026 | 2019-11-08 | 2 - Good | The door openers are in a fair condition overall, lifecycle replacement can be deferred. | 4 | Each | 3743.74 | 1.3 | 1.15 | 1 | 22387.57 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 279 | B301028 - Metal Roofing | B301028 | Metal Roofing | The building has an inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2022 | 40 | 2062 | 2057 | 2019-11-08 | 1 - Excellent |  | 780 | SF | 24.39 | 1.3 | 1.15 | 1 | 28441.18 | 0 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 281 | B301030 - Slate Roofing | B301030 | Slate Roofing | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2023 | 50 | 2073 | 2098 | 2019-11-08 | 1 - Excellent |  | 750 | SF | 30.47 | 1.3 | 1.15 | 1 | 34164.49 | 0 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 206 | Bamboo Panel Ceiling | C301022 | Wood Wall Finish | The building&rsquo;s ceiling finishes include bamboo ceiling finish. | 2012 | 25 | 2037 | 2042 | 2019-11-08 | 1 - Excellent | The ceiling finish is in good condition overall, no major deficiencies were observed. | 915 | SF | 23.54 | 1.3 | 1.15 | 1 | 32200.95 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 205 | Bamboo Panels | C301099 | Other Wall Finishes | The building includes bamboo panels located in lounges and as decorative accents throughout the building. | 2012 | 30 | 2042 | 2042 | 2019-11-08 | 1 - Excellent | No major deficiencies were observed or reported. | 5 | Lump Sum | 3850 | 1.3 | 1.15 | 1 | 28778.75 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 280 | C301021 - Wall Paper | C301021 | Wall Paper | The building's interior finishes include wall paper | 2021 | 20 | 2041 | 2036 | 2019-11-08 | 1 - Excellent |  | 4200 | SF | 5.51 | 1.3 | 1.15 | 1 | 34597.29 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 282 | C302002 - Terrazzo | C302002 | Terrazzo Floor | Terrazzo. | 2023 | 50 | 2073 | 2073 | 2019-11-08 | 1 - Excellent |  | 441 | SF | 39.13 | 1.3 | 1.15 | 1 | 25798.21 | 0 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 269 | Capacitor System | D509099 | Other Electrical Systems | The electrical system is provided with two 400kVAR, 600V, Power Survey, power factor correcting capacitor units; and a 313A, 600V, Square D, ReactiVar, harmonic filter unit. | 2012 | 20 | 2032 | 2032 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 3 | Lump Sum | 7700 | 1.3 | 1.15 | 1 | 34534.5 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 242 | Carpet | C302005 | Carpet Floor | The building's floor finishes include broadloom carpet located on the 300 floor. | 2005 | 10 | 2015 | 2026 | 2019-11-08 | 2 - Good | The carpet is in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 2422 | SF | 7.87 | 1.3 | 1.15 | 1 | 28496.4 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 272 | Carpet Tiles | C302005 | Carpet Floor | The buildings floor finishes include carpet tiles located in some of the offices. | 2018 | 10 | 2028 | 2028 | 2019-11-08 | 2 - Good | The carpet tiles are in good condition overall, no deficiencies were observed. | 2476 | SF | 7.87 | 1.3 | 1.15 | 1 | 29131.75 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 266 | Ceramic glass | C101005 | Interior Windows | The interior windows include fireproof ceramic glazed windows located on the 5th floor. | 2012 | 75 | 2087 | 2062 | 2019-11-08 | 1 - Excellent | The windows are in good condition overall, no deficiencies were observed. | 441 | SF | 52.22 | 1.3 | 1.15 | 1 | 34428.38 | 0 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 210 | Clean Steam Generator | D302003 | Fuel-Fired Forced Air Furnaces | The HVAC system is provided with a 4,000 lb/hr, clean steam generator. It is a steam-to-steam heat exchanger to convert "dirty" steam supplied from one of the steam boilers to "clean steam" with RO water for building humidification. | 2012 | 18 | 2030 | 2042 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 200 | MBH | 49.28 | 1.3 | 1.15 | 1.7 | 25049.02 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 213 | Condensing Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for the outside walk in cooler is provided by a 4 ton condensing unit. | 2008 | 18 | 2026 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 3743.74 | 1.3 | 1.15 | 1 | 22387.57 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 234 | Domestic Water Distribution - Backflow Preventer - 2012 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4 inch backflow preventer installed in 2012. | 2012 | 40 | 2052 | 2052 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 5382 | SF Building | 3.65 | 1.3 | 1.15 | 1 | 29368.23 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 209 | Electric Water Heater - 2014 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a 284L, 4500W, electric, water heater, JOHN WOOD, model: JW80SDE14S. | 2014 | 20 | 2034 | 2025 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 249 | Emergency Battery Pack Lights | D509003 | Emergency Lighting Systems | The emergency lighting system in some areas includes self-contained battery packs and lights. | 2010 | 20 | 2030 | 2030 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 37954 | SF Building | 0.5 | 1.3 | 1.15 | 1 | 28370.62 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 221 | Emergency Eyewash Units and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 25 | 2025 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Per Lavatory | 7487.48 | 1.3 | 1.15 | 1 | 33581.35 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 271 | Emergency lighting | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights. | 2007 | 20 | 2027 | 2027 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. | 46220 | SF Building | 0.5 | 1.3 | 1.15 | 1 | 34549.45 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 207 | Epoxy Painted Ceiling | C303006 | Painted Ceiling Structures | The building&rsquo;s ceiling finishes include epoxy paint finish located in the Phytotron, CL3, and, animal lab areas. | 2012 | 15 | 2027 | 2027 | 2019-11-08 | 2 - Good | No deficiencies were observed or reported. | 7320 | SF | 2.65 | 1.3 | 1.15 | 1 | 29000.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 214 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The HVAC exhaust ventilation system includes centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1998 | 25 | 2023 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. There is damage to one fan, the sheet metal shroud should be repaired under normal maintenance. | 6 | Each | 2808.19 | 1.3 | 1.15 | 1 | 25189.46 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 219 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The exhaust system consists of centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2000 | 25 | 2025 | 2025 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. | 8 | Each | 2808.19 | 1.3 | 1.15 | 1 | 33585.95 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 241 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The HVAC exhaust ventilation system centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2000 | 25 | 2025 | 2025 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. | 6 | Each | 2808.19 | 1.3 | 1.15 | 1 | 25189.46 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 248 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The HVAC exhaust ventilation system centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1990 | 25 | 2015 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 6 | Each | 2808.19 | 1.3 | 1.15 | 1 | 25189.46 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 255 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The HVAC system is provided with centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1994 | 25 | 2019 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 2808.19 | 1.3 | 1.15 | 1 | 33585.95 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 235 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1972 | 25 | 1997 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 5 | Each | 4679.29 | 1.3 | 1.15 | 1 | 34977.69 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 226 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with Exit Signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 1972 | 35 | 2007 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 800 | SF | 20.89 | 1.3 | 1.15 | 1 | 24984.44 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 230 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with exit signs on exit doors that includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2000 | 35 | 2035 | 2035 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 800 | SF | 20.89 | 1.3 | 1.15 | 1 | 24984.44 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 252 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with exit signs to indicated the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2000 | 35 | 2035 | 2035 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. Replacement can be deferred. | 800 | SF | 20.89 | 1.3 | 1.15 | 1 | 24984.44 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 220 | Exterior Hollow Metal Door - Single Leaf | B203023 | Exterior - Single Door - Hollow Metal | The exterior doors consist of hollow metal single-doors mounted by butt hinges to metal door frames. | 1972 | 30 | 2002 | 2026 | 2019-11-08 | 2 - Good | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 5 | Each | 2995.3 | 1.3 | 1.15 | 1 | 22389.87 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 232 | Exterior Storefront Door - Double Leaf | B203028 | Exterior - Double Door - Aluminum and Glass | The exterior doors consist of hollow metal glazed double -doors mounted by butt hinges to metal frames. | 1972 | 35 | 2007 | 2026 | 2019-11-08 | 2 - Good | The exterior doors are in fair condition overall and functioning as intended. Lifecycle replacement can be deferred. | 2 | Each | 8423.03 | 1.3 | 1.15 | 1 | 25184.86 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 250 | Exterior Storefront Door - Double Leaf | B203028 | Exterior - Double Door - Aluminum and Glass | The exterior doors consist of glass metal framed double-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 1982 | 35 | 2017 | 2026 | 2019-11-08 | 2 - Good | The exterior doors are in fair condition overall, lifecycle replacement can be deferred. | 2 | Each | 8423.03 | 1.3 | 1.15 | 1 | 25184.86 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 236 | Exterior Storefront Door - Single Leaf | B203028 | Exterior - Double Door - Aluminum and Glass | The exterior doors consist of hollow metal glazed single -doors mounted by butt hinges to metal door frames. | 1972 | 35 | 2007 | 2026 | 2019-11-08 | 2 - Good | The exterior doors have aged but they are in a fair condition overall, life cycle replacement can be deferred. | 2 | Each | 8423.03 | 1.3 | 1.15 | 1 | 25184.86 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 215 | Fan-coil Units | D305003 | Fan Coil Units | HVAC distribution includes a number of fan-coil units in the corridors near the entrances. | 1998 | 25 | 2023 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 4889.5 | 1.3 | 1.15 | 1 | 29239.21 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 263 | Fixed Casework - Kitchen Cabinets | C103010 | Vanities | Building includes kitchen cabinets including wall and under-counter cabinets and plastic laminate countertops, without appliances. | 2007 | 25 | 2032 | 2037 | 2019-11-08 | 1 - Excellent | The millwork is in good condition overall, no significant deficiencies were observed. | 98 | LF | 171.33 | 1.3 | 1.15 | 1 | 25101.56 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 227 | Foundation Wall and Footings | A101002 | Low Rise - 1 - 3 Level Building Foundation | The building is a three -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1972 | 75 | 2047 | 2047 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed or reported. | 12114 | SF Footprint | 23.11 | 1.3 | 1.15 | 1 | 418532.04 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 231 | Foundation Wall and Footings | A202002 | Basement Walls | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1972 | 75 | 2047 | 2047 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed or reported. | 2232 | SF Footprint | 34.69 | 1.3 | 1.15 | 1 | 115754.98 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 268 | Glazed Double Doors | C102005 | Interior - Overhead Doors - Standard | The building&rsquo;s interior doors include glazed double doors with wood frame located in room 209. | 2012 | 25 | 2037 | 2052 | 2019-11-08 | 1 - Excellent | The doors are in good condition overall, no major deficiencies observed. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 267 | Glazed Guardrails | C101028 | Interior Guardrails and Screens | The building includes glazed guardrails located on the 3rd floor corridor. | 2012 | 50 | 2062 | 2062 | 2019-11-08 | 1 - Excellent | The glazed guardrails are in good condition overall, no major deficiencies were observed. | 82 | LF | 285.39 | 1.3 | 1.15 | 1 | 34985.96 | 0 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 239 | Gypsum Board Ceiling | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 15 | 1987 | 2026 | 2019-11-08 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 9042 | SF | 2.65 | 1.3 | 1.15 | 1 | 35822.14 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 258 | Interior Automatic Openers - Single | C102007 | Interior - Automatic Door Openers | The building includes automatic openers for single swing doors located at the universal washrooms. | 2007 | 15 | 2022 | 2025 | 2019-11-08 | 2 - Good | The automatic door openers are in good condition and are functioning as intended. Lifecycle replacement can be deferred. | 4 | Each | 3743.74 | 1.3 | 1.15 | 1 | 22387.57 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 216 | Interior Doors - Special | C102099 | Other Interior Doors | The building includes copper shielded doors locate on the 400 floor. | 1972 | 40 | 2012 | 2026 | 2019-11-08 | 2 - Good | The copper shielded doors are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 5 | Lump Sum | 3850 | 1.3 | 1.15 | 1 | 28778.75 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 208 | Kitchenette Sinks | D201004 | Sinks | Plumbing fixtures include stainless steel sinks. | 2012 | 35 | 2047 | 2047 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 24 | Each | 977.9 | 1.3 | 1.15 | 1 | 35087.05 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 217 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 23 | Each | 977.9 | 1.3 | 1.15 | 1 | 33625.09 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 229 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system includes wall mounted HID fixtures, around the perimeter of the building which includes conduit and wire. | 1990 | 35 | 2025 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 6500 | SF | 2.65 | 1.3 | 1.15 | 1 | 25751.38 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 257 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system recessed mounted fixtures, lamps, conduit and wire. | 2000 | 35 | 2035 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 7000 | SF | 2.65 | 1.3 | 1.15 | 1 | 27732.25 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 264 | Loading Dock Equipment | E103003 | Loading Dock Truck Levellers | The building includes a loading dock leveler. | 2007 | 20 | 2027 | 2027 | 2019-11-08 | 2 - Good | No significent deficiencies were observed. | 1 | Each | 18717.16 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 202 | Mechanical Equipment Screens | B301028 | Metal Roofing | The building includes metal framed mechanical equipment screens located on the roof. | 2012 | 40 | 2052 | 2037 | 2019-11-08 | 1 - Excellent | The screens are in good condition overall, no major deficiencies were observed or reported. | 755 | SF | 24.39 | 1.3 | 1.15 | 1 | 27529.6 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 224 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 2000 | 40 | 2040 | 2040 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 10764 | SF | 1.86 | 1.3 | 1.15 | 1 | 29931.45 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 278 | Painted Concrete | C302007 | Painted / Sealed Floor | The building&rsquo;s floor finishes include painted/sealed floor finish located in the Mechanical rooms. | 2007 | 15 | 2022 | 2026 | 2019-11-08 | 2 - Good | The painted floor finish is in excellent condition, no significant deficiencies were observed. | 4790 | SF | 3.65 | 1.3 | 1.15 | 1 | 26137.83 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 265 | Retractable security gates | C101023 | Retractable Partitions - Folding Panel | The building&rsquo;s interior partitions include retractable security gates. | 2012 | 25 | 2037 | 2037 | 2019-11-08 | 1 - Excellent | The retractable security gates are in good condition overall and are functioning as intended. | 125 | SF | 147.86 | 1.3 | 1.15 | 1 | 27631.34 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 275 | Retractable security gates | C101023 | Retractable Partitions - Folding Panel | The building includes retractable security gates located in the 200 floor custodial office | 2000 | 25 | 2025 | 2025 | 2019-11-08 | 2 - Good | The retractable gates are in good condition overall, no significant deficiencies were observed. | 125 | SF | 147.86 | 1.3 | 1.15 | 1 | 27631.34 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 276 | Roof top stairs | C201002 | Exterior (Attached) Stair Construction | The building includes wood framed stairs that provide access to the fume hoods. | 1982 | 40 | 2022 | 2026 | 2019-11-08 | 2 - Good | The stairs have aged but are functioning as intended. Lifecycle replacement can be deferred. | 20 | Per Riser | 936.32 | 1.3 | 1.15 | 1 | 27995.97 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 212 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1998 | 20 | 2018 | 2025 | 2019-11-08 | 2 - Good | The wayfinding signage is in good condition overall, lifecycle replacement can be deferred. | 25855 | SF Building | 0.64 | 1.3 | 1.15 | 1 | 24738.06 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 237 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1997 | 20 | 2017 | 2012 | 2019-11-08 | 5 - Critical | The wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 27857 | SF Building | 0.64 | 1.3 | 1.15 | 1 | 26653.58 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 254 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1994 | 20 | 2014 | 2025 | 2019-11-08 | 2 - Good | The wayfinding signs have aged and need to be updated. Lifecycle replacement is recommended. | 24111 | SF Building | 0.64 | 1.3 | 1.15 | 1 | 23069.4 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 253 | Skylights | B302021 | Skylights | The building includes skylights with aluminum frame and double-pane insulated glazing. | 1994 | 25 | 2019 | 2025 | 2019-11-08 | 2 - Good | The skylights are in good condition overall, no deficiencies were observed. | 172 | SF | 136.27 | 1.3 | 1.15 | 1 | 35040.47 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 203 | Small Lower Roofs | B301023 | Conventional - Single Ply Membrane | Built-up roofing with black rubberized flood coat and black aggregate surfacing system on the small lower roofs. | 2012 | 20 | 2032 | 2032 | 2019-11-08 | 1 - Excellent | The lower roof is good condition, no deficiencies were observed or reported. | 1378 | SF | 16.1 | 1.3 | 1.15 | 1 | 33167.77 | 2 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 259 | Solid doors- Double | C102024 | Interior - Double Door - Hollow Metal | The building&rsquo;s interior doors include hollow metal and wood doors with vision panels. | 2007 | 30 | 2037 | 2047 | 2019-11-08 | 1 - Excellent | The interior doors are in good condition overall, no major deficiencies were observed or reported. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 244 | Sump Pump - Submersible - 1/2 HP | D203001 | Sanitary Waste and Vent Piping and Fittings | The water drainage system includes a duplex stormwater sump pump system. | 1997 | 50 | 2047 | 2047 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 3735 | SF Building | 4.15 | 1.3 | 1.15 | 1 | 23172.87 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 225 | Transformer - 45 KVA | D501026 | Grounding Methods | The building is equipped with a 45 kVA, 600V - 208Y/120V, 3-Phase, transformer on each floor. | 1972 | 50 | 2022 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 9358.58 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 228 | Transformers - 45 KVA - 1972 | D501026 | Grounding Methods | The building is equipped with a 45 KVA, 600V - 208Y/120V transformer on each floor. | 1972 | 50 | 2022 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 9358.58 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 274 | Transformers - 45 KVA - 2008 | D501026 | Grounding Methods | The building is equipped with a 45 KVA, 600V - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 9358.58 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 247 | Variable Frequency Drives - Air Handling Units | D501025 | Main Service Disconnects | The supply and return fan motors for the air handling units serving the G-Block are each equipped with a variable frequency drive. | 2013 | 40 | 2053 | 2033 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 9358.58 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 251 | Variable Frequency Drives - Air Handling Units | D501025 | Main Service Disconnects | The supply and return fan motors for the air handling unit are each equipped with a variable frequency drive. | 2010 | 40 | 2050 | 2030 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 9358.58 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 256 | Variable Frequency Drives - Air Handling Units | D501025 | Main Service Disconnects | The supply and return fan motors for the air handling unit are each equipped with a variable frequency drive. | 2010 | 40 | 2050 | 2030 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 9358.58 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 262 | Variable Frequency Drives - Air Handling Units | D501025 | Main Service Disconnects | The supply and return fan motors for the air handling units and the heat recovery units HRU-1 are each equipped with a variable frequency drive. | 2007 | 40 | 2047 | 2027 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. | 2 | Each | 9358.58 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 233 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Plank Floor | The building's floor finish includes asbestos containing vinyl tiles. | 1972 | 15 | 1987 | 2026 | 2019-11-08 | 2 - Good | The vinyl tiles are in fair condition overall, lifecycle replacement can be deferred. Cost includes a factor for abatement. | 1399 | SF | 9.08 | 1.3 | 1.15 | 1.5 | 28486.3 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 260 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include VCT tiles located in the lunch room (201) and electrical rooms. | 2007 | 15 | 2022 | 2025 | 2019-11-08 | 2 - Good | The vinyl tiles are in a fair condition overall, lifecycle replacement can be deferred. | 2076 | SF | 9.08 | 1.3 | 1.15 | 1 | 28180.87 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 277 | Vinyl Tiles | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include vinyl tiles located in room J205 and 300 floor corridor. | 2009 | 15 | 2024 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 2196 | SF | 9.08 | 1.3 | 1.15 | 1 | 29809.82 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 270 | Walk-in Coolers and Freezers | E109002 | Basketball Backboards - Fixed | The building is provided with walk-in coolers and freezers. | 2012 | 30 | 2042 | 2032 | 2019-11-08 | 1 - Excellent | No significant deficiencies were observed. | 4 | Each | 4679.29 | 1.3 | 1.15 | 1 | 27982.15 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 240 | Water Heater - 2015 - 322 L | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by an 85-gallon Rheem residential grade electric water heater rated at 15000 W. | 2015 | 20 | 2035 | 2027 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 246 | Water Heater - 80 Gallon - 1972 | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 323 L (85 gal) RUUD, electric, water heater rated at 45000 W. | 1972 | 20 | 1992 | 2022 | 2019-11-08 | 3 - Fair | This equipment has been in service 35 years beyond its rated useful life and the staff has reported that spare parts are difficult to obtain. Replacement is recommended. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 245 | Water Heater - 85 Gallon - 2011 | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 322 L (85 gal), RHEEM RUUD, electric, water heater rated at 45000 W. | 2011 | 20 | 2031 | 2027 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 222 | Water Heater - Domestic Hot Water | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water for the building is provided by a RHEEM, 322-Liter (85-gallon), electric, water heater rated at 15000 W located in the custodial room C214. | 2015 | 20 | 2035 | 2027 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 218 | Water Heater - Elec - 85 Gal | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided from a RHEEM, 322-Liter (85-gallon), electric, water heater rated at 24000 W. | 2006 | 20 | 2026 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 223 | Water Heater - Fish Lab | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water for the fish lab is provided by a RHEEM, 322-liter (85-gallon), water heater rated at 15000 W. | 2015 | 20 | 2035 | 2027 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 05.855 | 3 | Lysaker Gym | Crookston | 261 | Water Heater - Gas - 76 Gallon | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 288L (76-gal), John Wood, gas fired, water heater rated at 72MBH. | 2012 | 20 | 2032 | 2026 | 2019-11-08 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 5615.61 | 1.3 | 1.15 | 1 | 25186.01 | 1 | Active |  |  |  |  | Athletics | East
| 01.074 | 4 | Mayo Building | Minneapolis | 911 | 2025-Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling located in the corridors. | 2026 | 15 | 2041 | 2040 |  | 1 - Excellent |  | 8800 | SF | 2.65 | 1.3 | 1 | 1.6 | 48505.6 | 0 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 338 | Acoustic Tile Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | Ceiling finishes located in some offices on the 300 floor level include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2005 | 25 | 2030 | 2025 | 2019-10-16 | 2 - Good | The ceiling tiles are in good condition overall, no significant deficiencies were observed. | 4198 | SF | 7.87 | 1.3 | 1 | 1 | 42949.74 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 283 | Aluminum-Framed Storefronts | B203028 | Exterior - Double Door - Aluminum and Glass | The building includes aluminum framed glazed double-doors with tempered glass door leafs located at the main entrance vestibules. | 2012 | 35 | 2047 | 2022 | 2019-10-16 | 3 - Fair | The exterior door frames are designed to handle 200 lb doors, however these doors are 300 lbs and are slowly failing. | 4 | Each | 8423.03 | 1.3 | 1 | 1 | 43799.76 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 285 | Automatic Sliding Doors - East and Northwest Entrances | B203021 | Exterior - Overhead Doors - Standard | The building&rsquo;s exterior doors include automatic sliding doors located at the Northeast side of the building. | 2014 | 25 | 2039 | 2044 | 2019-10-16 | 1 - Excellent | The exterior doors are in good condition overall, no major deficiencies were observed. | 4 | Each | 5615.61 | 1.3 | 1 | 1 | 29201.17 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 370 | B203006 - Glazed Doors - Double | B203028 | Exterior - Double Door - Aluminum and Glass | The building includes aluminum framed glazed double-doors with tempered glass door leafs located at the main entrance vestibules. | 2023 | 35 | 2058 | 2048 | 2019-10-16 | 1 - Excellent |  | 4 | Each | 8423.03 | 1.3 | 1 | 1 | 43799.76 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 289 | Building and Washroom Exhaust Fans | E102007 | Fume Hood Systems | General building and washroom exhaust consists of roof mounted and in-line exhaust fans with ducting. | 2012 | 25 | 2037 | 2037 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 6 | Each | 4679.29 | 1.3 | 1 | 1 | 36498.46 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 371 | C301005 - Painted Wall Covering | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, and concrete walls. | 2023 | 10 | 2033 | 2033 | 2019-10-16 | 1 - Excellent |  | 8000 | SF Building | 3.65 | 1.3 | 1 | 1 | 37960 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 921 | C302002 - Terrazzo Floor | C302002 | Terrazzo Floor | The building includes broadloom carpet provided in some offices. | 2025 | 50 | 2075 | 2075 |  | 3 - Fair |  | 2640 | SF | 39.13 | 1.3 | 1 | 1 | 134294.16 | 0 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 368 | C302005 - Carpet | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the laboratories and the corridors. | 2022 | 10 | 2032 | 2032 | 2019-10-16 | 1 - Excellent |  | 1900 | SF | 7.87 | 1.3 | 1 | 2 | 38877.8 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 922 | C302023 - Vinyl Sheet Floor | C302023 | Vinyl Sheet Floor | The building includes broadloom carpet provided in some offices. | 2025 | 15 | 2040 | 2040 |  | 3 - Fair |  | 2634 | SF | 10.94 | 1.3 | 1 | 1 | 37460.75 | 0 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 308 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the offices. | 2015 | 10 | 2025 | 2026 | 2019-10-16 | 2 - Good | The carpet tiles are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 5242 | SF | 7.87 | 1.3 | 1 | 1 | 53630.9 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 363 | Carpet tiles | C302005 | Carpet Floor | The building includes carpet tile flooring located on the 300 floor | 2014 | 10 | 2024 | 2026 | 2019-10-16 | 2 - Good | The carpet tiles are in good condition overall, lifecycle replacement can be deferred. | 3552 | SF | 7.87 | 1.3 | 1 | 1 | 36340.51 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 365 | Carpet tiles | C302005 | Carpet Floor | The buildings floor finishes include carpet tiles located in pond inlet hall. | 2016 | 10 | 2026 | 2026 | 2019-10-16 | 2 - Good | The carpet tiles are in good condition overall, no deficiencies were observed. | 3563 | SF | 7.87 | 1.3 | 1 | 1 | 36453.05 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 303 | Chiller | D303003 | Water Cooled Chillers | Cooling medium is provided by a TRANE, air cooled, chiller installed on the roof with a cooling capacity of 30 tons. | 2010 | 30 | 2040 | 2035 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 30 | Ton | 1123.43 | 1.3 | 1 | 1 | 43813.77 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 293 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 1998 | 25 | 2023 | 2026 | 2019-10-16 | 2 - Good | The washrooms are in fair condition, lifecycle replacement can be deferred. | 1 | Per Lavatory | 23396.45 | 1.3 | 1 | 1 | 30415.39 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 373 | Conventional BUR | B301021 | Conventional - Built-Up Roof | The flat roof structure has a conventional roof assembly system, where the roof membrane is a multi-ply built-up roof membrane protected by a white flood coat and white aggregate surfacing system. Gravel stops completed with pre-finished metal cap flashing are provided at the roof perimeter. | 2023 | 22 | 2045 | 2045 | 2019-10-16 | 1 - Excellent |  | 1500 | SF | 17.45 | 1.3 | 1 | 1 | 34027.5 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 334 | D3042 - Exhaust Ventilation Systems - Room G200 Cryogenic Nitrogen | D305001 | Unit Ventilators | Cryogenic nitrogen is handled in Room G200. Ventilation system was added in 2015 for 28K. | 2015 | 25 | 2040 | 2040 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 11230.45 | 1.3 | 1 | 2.34 | 34163.03 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 364 | Distribution Transformer - 300kVA | D501026 | Grounding Methods | The electrical system for the building is provided with a 300kVA, 600V - 208Y/120V, 3-Phase transformer. | 1972 | 50 | 2022 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 9358.58 | 1.3 | 1 | 1 | 48664.62 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 298 | Domestic Water Tank - 435 Litre | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided from a 435 liter, Rheem Rhuud, domestic cold water storage tank. | 2010 | 20 | 2030 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 5 | Each | 5615.61 | 1.3 | 1 | 1 | 36501.47 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 354 | Drinking Water Fountains | D201006 | Drinking Water Fountains (Non-refrigerated) | The building is provided with ELKAY EZH2O drinking water fountains. | 2012 | 30 | 2042 | 2042 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 24 | Each | 1466.85 | 1.3 | 1 | 1 | 45765.72 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 349 | DX Condensing Units | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling medium is provided by three condensing units, CU-1, CU-2 & CU-3, each having a cooling capacity of 2.5 tons. | 2007 | 18 | 2025 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 3743.74 | 1.3 | 1 | 1 | 38934.9 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 322 | Emergency Battery Pack Lights | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights in the corridors and the egress passages. | 2010 | 20 | 2030 | 2030 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 63701 | SF Building | 0.5 | 1.3 | 1 | 1 | 41405.65 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 342 | Emergency Battery Pack Lights | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights in selected areas. | 2010 | 20 | 2030 | 2030 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 68781 | SF Building | 0.5 | 1.3 | 1 | 1 | 44707.65 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 348 | Emergency Eyewash and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed in the sixth floor Mechanical Penthouse and the janitor rooms. | 2007 | 25 | 2032 | 2027 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. | 4 | Per Lavatory | 7487.48 | 1.3 | 1 | 1 | 38934.9 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 296 | Emergency Eyewash Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and shower stations installed throughout the building in the labs. | 1998 | 25 | 2023 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Per Lavatory | 7487.48 | 1.3 | 1 | 1 | 38934.9 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 319 | Emergency Eyewash Units and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 25 | 2025 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Per Lavatory | 7487.48 | 1.3 | 1 | 1 | 38934.9 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 309 | Epoxy Flooring | C302007 | Painted / Sealed Floor | The building's floor finishes include epoxy floor finish located in the laboratories. | 2000 | 15 | 2015 | 2026 | 2019-10-16 | 2 - Good | The floor finish is in good condition overall, lifecycle replacement can be deferred. | 9688 | SF | 3.65 | 1.3 | 1 | 1 | 45969.56 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 290 | Exhaust Fans | E102007 | Fume Hood Systems | The HVAC system is provided with 48,550CFM, Strobic Air, Tri-Stack, 75hp, roof-mounted, exhaust fans. | 2012 | 25 | 2037 | 2037 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 7 | Each | 4679.29 | 1.3 | 1 | 1 | 42581.54 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 312 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The HVAC exhaust ventilation system consists of centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2000 | 25 | 2025 | 2025 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. | 10 | Each | 2808.19 | 1.3 | 1 | 1 | 36506.47 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 320 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The HVAC system is provided with centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 1997 | 25 | 2022 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 12 | Each | 2808.19 | 1.3 | 1 | 1 | 43807.76 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 350 | Exhaust System - Fans - General Building | D304031 | Exhaust Fans - Centrifugal | The HVAC equipment is provided with an exhaust ventilation system with centrifugal and in-line exhaust fans installed on the roof and throughout the building. | 2007 | 25 | 2032 | 2032 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 12 | Each | 2808.19 | 1.3 | 1 | 1 | 43807.76 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 299 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. Note: System cost represents a 6 foot long fume hood. | 1998 | 25 | 2023 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 4679.29 | 1.3 | 1 | 1 | 48664.62 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 313 | Exhaust System - Fume Hood - Ductwork/Fan (Each) | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood exhaust systems with ducting. | 1990 | 25 | 2015 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 7 | Each | 4679.29 | 1.3 | 1 | 1 | 42581.54 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 284 | Exterior Doors - Automatic Door Operators | B203008 | Exterior - Automatic Door Openers | Automatic door operators are provided a the main entrance vestibules. | 2012 | 15 | 2027 | 2027 | 2019-10-16 | 2 - Good | The automatic door openers are functioning as intended, no major deficiencies were observed. | 9 | Each | 3743.74 | 1.3 | 1 | 1 | 43801.76 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 292 | Exterior Storefront Door - Double Leaf | B203028 | Exterior - Double Door - Aluminum and Glass | The building's exterior doors includes aluminum framed glazed double doors. | 1998 | 35 | 2033 | 2025 | 2019-10-16 | 2 - Good | The exterior doors are in good condition overall and functioning as intended, lifecycle replacement can be deferred. | 3 | Each | 8423.03 | 1.3 | 1 | 1 | 32849.82 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 318 | Exterior Storefront Door - Double Leaf | B203028 | Exterior - Double Door - Aluminum and Glass | The exterior doors consist of hollow metal glazed double -doors mounted by butt hinges to metal door frames. | 1972 | 35 | 2007 | 2038 | 2019-10-16 | 1 - Excellent | The exterior doors have aged and are in poor condition, lifecycle replacement is recommended. | 3 | Each | 8423.03 | 1.3 | 1 | 1 | 32849.82 | 2 | Active | 380 |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 337 | Exterior Storefront Door - Single Leaf | B203005 | Exterior - Hangar Doors | The exterior doors consist of glass metal framed single-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 1982 | 25 | 2007 | 2026 | 2019-10-16 | 2 - Good | The exterior doors are in fair condition overall, lifecycle replacement can be deferred. | 4 | Lump Sum | 7700 | 1.3 | 1 | 1 | 40040 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 286 | Fibreglass Reinforced Polyester Door | C102021 | Interior - Single Door - Hollow Metal | Fiberglass reinforced polyester door with stainless steel frames, some with glass lites are provided at rooms 569 & 576. | 2012 | 40 | 2052 | 2052 | 2019-10-16 | 1 - Excellent | No deficiencies were observed or reported. | 12 | Each | 2340.03 | 1.3 | 1 | 1 | 36504.47 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 327 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building iis provided with a fire alarm system which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 6415 | SF Building | 4.58 | 1.3 | 1 | 1 | 38194.91 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 328 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system which includes a maim fire alarm control panel, an annunciator panel at the main entrance, and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 6415 | SF Building | 4.58 | 1.3 | 1 | 1 | 38194.91 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 329 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes all conduit, wire, and connections to the main control panel, annunciation panel, pull stations, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. No photo is available. | 6415 | SF Building | 4.58 | 1.3 | 1 | 1 | 38194.91 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 306 | Fixed Casework - Lab Benches | E201003 | Bleachers | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1972 | 25 | 1997 | 2026 | 2019-10-16 | 2 - Good | The millwork is in fair condition overall, lifecycle replacement can be deferred. | 70 | Per Seat | 515.13 | 1.3 | 1 | 1 | 46876.83 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 316 | Fixed Casework - Lab Benches | C103011 | Millwork General | The building includes metal lab benches with acid resistant countertops. | 1972 | 25 | 1997 | 2022 | 2019-10-16 | 3 - Fair | The millwork has aged and is in poor condition, lifecycle replacement is recommended. | 6781 | SF Building | 5.22 | 1.3 | 1 | 1 | 46015.87 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 323 | Fixed Casework - Lab Benches | C103011 | Millwork General | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1972 | 25 | 1997 | 2026 | 2019-10-16 | 2 - Good | The fixed caework is in fair condition overall, lifecycle replacement can be deferred. | 5167 | SF Building | 5.22 | 1.3 | 1 | 1 | 35063.26 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 326 | FM200 System - High Density | D409099 | Other Fire Protection Systems | The fire protection systems include a clean air PyroChem system for the server room. | 2010 | 20 | 2030 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Lump Sum | 7700 | 1.3 | 1 | 1 | 40040 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 332 | Foundation Wall and Footings | A202002 | Basement Walls | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1972 | 75 | 2047 | 2047 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 2520 | SF Footprint | 34.69 | 1.3 | 1 | 1 | 113644.44 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 346 | Foundation Wall and Footings - 14-ft. - Full Basement | A101003 | Mid Rise - 4 - 8 Level Building Foundation | The building is a five -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 2007 | 75 | 2082 | 2082 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 6057 | SF Footprint | 50.07 | 1.3 | 1 | 1 | 394256.19 | 0 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 366 | Fume Hoods | E102007 | Fume Hood Systems | The labs are provided with exhaust fume hoods with ducting. | 1982 | 25 | 2007 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 7 | Each | 4679.29 | 1.3 | 1 | 1 | 42581.54 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 353 | Glazed wall panels | C301099 | Other Wall Finishes | The building&rsquo;s wall finishes include glazed wall panels located near the main entrance. | 2012 | 30 | 2042 | 2042 | 2019-10-16 | 1 - Excellent | No major deficiencies were observed or reported. | 10 | Lump Sum | 3850 | 1.3 | 1 | 1 | 50050 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 294 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling located in the corridors. | 1998 | 15 | 2013 | 2025 | 2019-10-16 | 2 - Good | The GWB ceiling finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 3273 | SF | 2.65 | 1.3 | 1 | 1 | 11275.49 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 310 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 15 | 1987 | 2026 | 2019-10-16 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 12153 | SF | 2.65 | 1.3 | 1 | 1 | 41867.09 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 339 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include GWB ceiling located in the corridors. | 1982 | 15 | 1997 | 2026 | 2019-10-16 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 11410 | SF | 2.65 | 1.3 | 1 | 1 | 39307.45 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 295 | Handicap Lift - 3-Storey | D101004 | Wheelchair Lifts | The conveying equipment includes a 3-storey, hydraulic, 454Kg (1000LBS), handicap lift and is rated at 2.6 HP. | 1998 | 25 | 2023 | 2028 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 29335.46 | 1.3 | 1 | 1 | 38136.1 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 347 | Interior Coiling Counter Doors - 6' x 4' | C102006 | Interior - Overhead Doors - Industrial | The building&rsquo;s interior doors include coiling counter doors located in room 600B. | 2007 | 30 | 2037 | 2037 | 2019-10-16 | 1 - Excellent | The coiling doors are in good condition overall, no major deficiencies were observed. | 2 | Each | 11230.45 | 1.3 | 1 | 1 | 29199.17 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 324 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102024 | Interior - Double Door - Hollow Metal | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 1972 | 30 | 2002 | 2026 | 2019-10-16 | 2 - Good | The double doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 4 | Each | 5615.61 | 1.3 | 1 | 1 | 29201.17 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 343 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102024 | Interior - Double Door - Hollow Metal | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 1994 | 30 | 2024 | 2034 | 2019-10-16 | 1 - Excellent | The doors are in good condition overall, no significant deficiencies were observed. | 6 | Each | 5615.61 | 1.3 | 1 | 1 | 43801.76 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 344 | Interior Rolling Doors - | C102006 | Interior - Overhead Doors - Industrial | The building includes interior rolling doors located in the corridor. | 1994 | 30 | 2024 | 2025 | 2019-10-16 | 2 - Good | The doors are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 2 | Each | 11230.45 | 1.3 | 1 | 1 | 29199.17 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 330 | Interior Windows - Metal | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 300 floor. | 1972 | 75 | 2047 | 2026 | 2019-10-16 | 2 - Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 646 | SF | 52.22 | 1.3 | 1 | 1 | 43854.36 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 355 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System and includes main control panel, ultrasonic detectors, arming panels, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2015 | 20 | 2035 | 2035 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 35779 | SF Building | 0.93 | 1.3 | 1 | 1 | 43256.81 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 358 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System which includes main control panel, motion detectors, arming panels, wiring and conduit. | 2015 | 20 | 2035 | 2035 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 46220 | SF Building | 0.93 | 1.3 | 1 | 1 | 55879.98 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 297 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 2010 | 35 | 2045 | 2045 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 30 | Each | 977.9 | 1.3 | 1 | 1 | 38138.1 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 314 | Lighting Fixtures - Exterior | D502021 | Interior Lighting (Residential) | The exterior lighting system consists of surface and recessed mounted fixtures, conduit and wire. | 2000 | 35 | 2035 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 10000 | SF | 2.65 | 1.3 | 1 | 1 | 34450 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 369 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts including conduit and wire. | 2024 | 35 | 2059 | 2051 | 2019-10-16 | 1 - Excellent |  | 3526 | SF Building | 7.73 | 1.3 | 1 | 1 | 35432.77 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 359 | Mechanical equipment screens | B201005 | Exterior Louvers and Screens | The building includes corrugated metal mechanical equipment screen with metal frame. | 1972 | 50 | 2022 | 2026 | 2019-10-16 | 2 - Good | Uniform corrosion was observed on the mechanical equipment screen. Maintenance is recommended to extend the life of the screen which will be covered under the maintenance budget. | 463 | SF | 60.88 | 1.3 | 1 | 1 | 36643.67 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 361 | Metal Panel | B201028 | Insulated Metal Sandwich Panels | The building exterior wall includes insulated corrugated metal panel system located on the 200 floor. | 2005 | 40 | 2045 | 2056 | 2019-10-16 | 1 - Excellent | The exterior wall system is in good condition overall, no deficiencies were observed or reported. | 1109 | SF | 30.4 | 1.3 | 1 | 1 | 43827.68 | 0 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 360 | Motor Control Centres | D501024 | Main Service Panels | The electrical distribution system is provided with motor control centres for the supply and control of electrical power to HVAC equipment and other motor loads. | 1972 | 40 | 2012 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 12166.77 | 1.3 | 1 | 1 | 31633.6 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 345 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating in the washrooms and corridors. | 1994 | 18 | 2012 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 100 | Each | 293.37 | 1.3 | 1 | 1 | 38138.1 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 357 | Railings | B201007 | Exterior Guards and Railings | The building include aluminum walkway/ guardrails located on the rooftop. | 2005 | 25 | 2030 | 2030 | 2019-10-16 | 1 - Excellent | The System is in good condition overall, no deficiencies were observed. | 89 | LF | 298.06 | 1.3 | 1 | 1 | 34485.54 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 301 | Roof Mounted Steps and Walkway | B201007 | Exterior Guards and Railings | The roof includes a set of stairs with 6 steel plate treads, steel grate walkway and pipe railing. | 2010 | 25 | 2035 | 2050 | 2019-10-16 | 1 - Excellent | The steel grate walkway is in good condition overall, no significant deficiencies were observed. | 92 | LF | 298.06 | 1.3 | 1 | 1 | 35647.98 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 372 | Section B - Green Roofing | B301032 | Green Roofing | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2024 | 30 | 2054 | 2054 | 2019-10-16 | 1 - Excellent |  | 850 | SF | 43.49 | 1.3 | 1 | 1 | 48056.45 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 305 | Security System - CCTV | D503008 | Intrusion Alarm Systems | The building is provided with a CCTV Security System which monitors points of egress and includes video recorder, monitoring station, cameras, conduit and cabling. | 2010 | 20 | 2030 | 2030 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 35779 | SF Building | 0.93 | 1.3 | 1 | 1 | 43256.81 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 315 | Security System - CCTV | D503008 | Intrusion Alarm Systems | The building is provided with a CCTV Security System that monitors points of egress and includes video recorder, monitoring station, cameras, conduit and cabling. | 2010 | 20 | 2030 | 2030 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 46220 | SF Building | 0.93 | 1.3 | 1 | 1 | 55879.98 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 302 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1972 | 20 | 1992 | 2025 | 2019-10-16 | 2 - Good | The building wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 37017 | SF Building | 0.64 | 1.3 | 1 | 1 | 30798.14 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 307 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1972 | 20 | 1992 | 1987 | 2019-10-16 | 5 - Critical | The wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 46220 | SF Building | 0.64 | 1.3 | 1 | 1 | 38455.04 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 333 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1972 | 20 | 1992 | 2022 | 2019-10-16 | 3 - Fair | The wayfinding signage has aged and exceeded its EUL, lifecycle replacement is recommended. | 37964 | SF Building | 0.64 | 1.3 | 1 | 1 | 31586.05 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 317 | Soffit - Plaster on Metal Lath | B201008 | Exterior Soffits | The building's overhang soffits are plaster-on-metal lath. | 2005 | 50 | 2055 | 2037 | 2019-10-16 | 1 - Excellent | The exterior soffit is in good condition overall, no deficiencies were observed. | 2217 | SF | 9.59 | 1.3 | 1 | 1 | 27639.34 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 311 | Split DX Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for the fish lab is provided by a Mitsubishi, cooling unit rated 6 tons. | 2008 | 18 | 2026 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 6 | Each | 3743.74 | 1.3 | 1 | 1 | 29201.17 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 288 | Split System A/C Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | A 7.5-ton, split system, LIEBERT, air conditioning unit serves the NMR room. | 2012 | 18 | 2030 | 2027 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. | 8 | Each | 3743.74 | 1.3 | 1 | 1 | 38934.9 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 340 | Sump Pump - Submersible - 1/2 HP | D203001 | Sanitary Waste and Vent Piping and Fittings | The water drainage system includes a duplex stormwater sump pump system.. | 2005 | 50 | 2055 | 2055 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 7126 | SF Building | 4.15 | 1.3 | 1 | 1 | 38444.77 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 291 | Suppression System | D409099 | Other Fire Protection Systems | The NMR is equipped with a Novec 1230 clean agent fire suppression system (482 lb of Novec 1230). | 2012 | 20 | 2032 | 2025 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Lump Sum | 7700 | 1.3 | 1 | 1 | 40040 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 300 | Transformer | D501026 | Grounding Methods | The building is equipped with a 300kVA, 600V - 208Y/120V, transformer. | 2008 | 50 | 2058 | 2048 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 4 | Each | 9358.58 | 1.3 | 1 | 1 | 48664.62 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 335 | Transformer - 225 KVA | D501026 | Grounding Methods | The building is equipped with a 225 KVA, 600V - 208Y/120V transformer that serves the Laboratory. | 2008 | 50 | 2058 | 2048 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 9358.58 | 1.3 | 1 | 1 | 36498.46 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 304 | Transformer - 75 KVA | D501026 | Grounding Methods | The building is equipped with three 75 KVA, 600V - 208Y/120V transformers. | 1972 | 50 | 2022 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 9358.58 | 1.3 | 1 | 1 | 36498.46 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 352 | Transformer - 75 KVA | D501026 | Grounding Methods | The building is equipped with three 75kVA, 600V - 208Y/120V, dry type transformers. | 2007 | 50 | 2057 | 2047 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 9358.58 | 1.3 | 1 | 1 | 36498.46 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 331 | Transformers - 75 KVA | D501026 | Grounding Methods | The building is equipped with a 75 KVA, 600Y - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 9358.58 | 1.3 | 1 | 1 | 36498.46 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 336 | Transformers - 75 KVA | D501026 | Grounding Methods | The building is equipped with a 75 KVA, 600V - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 9358.58 | 1.3 | 1 | 1 | 36498.46 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 321 | Transformers - 75 KVA - 1972 | D501026 | Grounding Methods | The building is equipped with a 75 KVA, 600V - 208Y/120V transformer on each floor. | 1972 | 50 | 2022 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 3 | Each | 9358.58 | 1.3 | 1 | 1 | 36498.46 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 362 | Transformers - 75 KVA - 2008 | D501026 | Grounding Methods | The building is equipped with a 75 KVA, 600V - 208Y/120V transformer on each floor. | 2008 | 50 | 2058 | 2048 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 9358.58 | 1.3 | 1 | 1 | 36498.46 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 351 | Unit Heaters - Hot Water | D305002 | Unit Heaters (Hydronic) | Heating for the mechanical penthouse and basement mechanical rooms is provided by suspended, forced hot water, unit heaters. | 2007 | 30 | 2037 | 2027 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. | 9 | Each | 2933.7 | 1.3 | 1 | 1 | 34324.29 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 287 | Urethane Flooring | C302007 | Painted / Sealed Floor | The building&rsquo;s floor finishes include Urethane flooring located in the animal and CL3 labs. | 2012 | 15 | 2027 | 2027 | 2019-10-16 | 2 - Good | The floor finish is in good condition overall, no deficiencies were observed. | 10925 | SF | 3.65 | 1.3 | 1 | 1 | 51839.13 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 341 | Water Dist Complete - Backflow Preventer - 2012 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes two (2) 4 inch backflow preventer installed in 2012, one on each of the two parallel lines. | 2012 | 40 | 2052 | 2052 | 2019-10-16 | 1 - Excellent | No significant deficiencies were observed. | 6878 | SF Building | 3.65 | 1.3 | 1 | 1 | 32636.11 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 325 | Water Heater - Elec - Residential - 85 Gallon | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a RHEEM, 322 Liter (85 gal), electric, water heater rated at 15000 W. | 2010 | 20 | 2030 | 2026 | 2019-10-16 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 5615.61 | 1.3 | 1 | 1 | 29201.17 | 1 | Active |  |  |  |  | Academic | East
| 01.074 | 4 | Mayo Building | Minneapolis | 367 | Wood panels | C301022 | Wood Wall Finish | The buildings wall finishes include wood panels provided on the 4th, 3rd and 2nd floors. | 2007 | 25 | 2032 | 2032 | 2019-10-16 | 1 - Excellent | The wall finishes are in good condition overall, no significant deficiencies were observed. | 1238 | SF | 23.54 | 1.3 | 1 | 1 | 37885.28 | 1 | Active |  |  |  |  | Academic | East
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 436 | Acid Proof Sheet Vinyl | C302021 | Rubber / Spring Gym Floor | The building's floor finishes include sheet vinyl located in rooms 212, 213, 220, 221 and 224. | 2014 | 20 | 2034 | 2034 | 2019-11-05 | 1 - Excellent | No deficiencies were observed or reported | 3993 | SF | 17.45 | 1.3 | 1 | 1 | 90581.21 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 434 | Aluminum Sash | B202001 | Windows | The buildings exterior windows are aluminum framed with insulating glass. | 1982 | 35 | 2017 | 2021 | 2019-11-05 | 4 - Poor | The windows have aged and have broken seals, life cycle replacement is recommended. | 646 | SF | 82.62 | 1.3 | 1 | 1 | 69384.28 | 2 | Active | 719 |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 375 | Aluminum-Framed Single Doors | B203005 | Exterior - Hangar Doors | The exterior doors consist of glazed aluminum framed single-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 2012 | 25 | 2037 | 2037 | 2019-11-05 | 1 - Excellent | The exterior doors are in good condition overall, no major deficiencies were observed. | 5 | Lump Sum | 7700 | 1.3 | 1 | 1 | 50050 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 417 | Auto Transfer Switch | D509002 | Emergency Power Generator Systems - Up to 300kVA | The emergency power system for this building includes an auto transfer switch for the essential load. The ATS is located in the main electrical vault. | 2001 | 30 | 2031 | 2037 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 104 | kVA | 421.19 | 1.3 | 1 | 1 | 56944.89 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 912 | B301024 - Inverted - Built-Up Roof | B301024 | Inverted - Built-Up Roof | The building's atrium is protected with a corrugated insulated metal standing seam roof cover. | 2025 | 30 | 2055 | 2055 |  | 2 - Good |  | 850 | SF | 20.03 | 1.3 | 1 | 1 | 22133.15 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 902 | B301030 - Slate Roofing | B301030 | Slate Roofing | The atrium is protected with a prefinished insulated metal standing seam roof cover. | 2023 | 50 | 2073 | 2073 |  | 2 - Good |  | 1275 | SF | 30.47 | 1.3 | 1 | 1 | 50504.03 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 439 | Boiler HW - Gas-Fired - 2010 | D302002 | Hot Water Boilers - Up to 1000 MBH | Heating medium is provided from a Fulton gas-fired steam boiler rated at approximately 500 MBH. | 2010 | 30 | 2040 | 2040 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 500 | MBH | 70.84 | 1.3 | 1 | 1 | 46046 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 466 | C302005 - Carpet | C302005 | Carpet Floor | Upgraded carpet and underpad installed - Second Phase in 2022 | 2022 | 10 | 2032 | 2035 | 2019-11-05 | 1 - Excellent |  | 9903 | SF | 7.87 | 1.3 | 1 | 1 | 101317.59 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 467 | C302006 - Vinyl Sheet | C302006 | Masonry and Stone Floor | Vinyl Sheer | 2023 | 50 | 2073 | 2038 | 2019-11-05 | 1 - Excellent |  | 1100 | SF | 51.36 | 1.3 | 1 | 1 | 73444.8 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 377 | Carpet Tile | C302005 | Carpet Floor | The building&rsquo;s floor finishes include carpet tile floor finish located in the offices | 2012 | 10 | 2022 | 2025 | 2019-11-05 | 2 - Good | The carpet tiles are in good condition overall, no major deficiencies were observed. Life cycle replacement can be deferred. | 8724 | SF | 7.87 | 1.3 | 1 | 1 | 89255.24 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 388 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet floor tiles located in the offices. | 2005 | 10 | 2015 | 2026 | 2019-11-05 | 2 - Good | The carpet tiles are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 9731 | SF | 7.87 | 1.3 | 1 | 1 | 99557.86 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 419 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the offices. | 2005 | 10 | 2015 | 2026 | 2019-11-05 | 2 - Good | The carpet tiles are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 8396 | SF | 7.87 | 1.3 | 1 | 1 | 85899.48 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 454 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tile flooring located in offices, conference rooms and miscellaneous spaces. | 2007 | 10 | 2017 | 2025 | 2019-11-05 | 2 - Good | The carpet tiles are in good condition overall, however stained tiles were observed in isolated locations which is covered under the maintenance budget. Lifecycle replacement can deferred. | 9726 | SF | 7.87 | 1.3 | 1 | 1 | 99506.71 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 455 | Central AHU - Air Handler - Heat Recovery Unit - HRU-1 - 25000 CFM | D304025 | Heat Exchangers - Plate and Frame | The HVAC system includes an ENG AIR, heat recovery unit (HRU-1) having a capacity of 2,5000 CFM. | 2007 | 30 | 2037 | 2032 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 46792.9 | 1.3 | 1 | 1 | 60830.77 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 446 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish. The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 1994 | 25 | 2019 | 2035 | 2019-11-05 | 1 - Excellent | The washrooms are in fair condition overall, no significant deficiencies were observed. | 2 | Per Lavatory | 23396.45 | 1.3 | 1 | 1 | 60830.77 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 386 | Concrete Masonry Unit Exterior Walls | B201021 | Masonry | The building's exterior wall include sections of concrete masonry unit. | 1972 | 75 | 2047 | 2047 | 2019-11-05 | 1 - Excellent | The exterior wall is in good condition overall, no significant deficiencies were observed or reported. | 754 | SF | 52.22 | 1.3 | 1 | 1 | 51186.04 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 461 | Curtain Wall | B202003 | Window Walls | The building includes a curtain wall system located on the roof. | 1972 | 40 | 2012 | 2026 | 2019-11-05 | 2 - Good | The curtain wall is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 560 | SF | 108.73 | 1.3 | 1 | 1 | 79155.44 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 458 | Curtain Walls | B202003 | Window Walls | The building includes a curtain wall system located on the roof. | 1972 | 40 | 2012 | 2026 | 2019-11-05 | 2 - Good | The curtain walls are in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 484 | SF | 108.73 | 1.3 | 1 | 1 | 68412.92 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 449 | DDC/Pneumatic System | D306006 | Direct Digital Control Systems | HVAC controls include a hybrid DDC/Pneumatic system with basic pc control, moderate sensor types and quantities as well as pneumatic activation of control valves and dampers. | 1994 | 20 | 2014 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 24111 | SF Building | 2.79 | 1.3 | 1 | 1 | 87450.6 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 415 | DDC/Pneumatic System - Hybrid - Average | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities as well as pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SF Building | 2.79 | 1.3 | 1 | 1 | 69845.14 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 440 | Distribution Equipment - Motor Control Centres | D501024 | Main Service Panels | The electrical distribution system is provided with motor control centres for the supply and control of electrical power to the HVAC equipment and other motor loads. | 1982 | 40 | 2022 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 4 | Each | 12166.77 | 1.3 | 1 | 1 | 63267.2 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 418 | Distribution Switchgears - 15kV, 600A | D501021 | Low Voltage Electrical Service | The electrical distribution system for the building is provided with a 15kV, 600A, switchgear assembly which includes fused interrupter switches, incoming and distribution feeders. | 1997 | 40 | 2037 | 2037 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 19257 | SF Building | 2.79 | 1.3 | 1 | 1 | 69845.14 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 412 | Domestic Water Distribution - 1972 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; for main branch piping, water meter, valves, insulation and fittings. | 1972 | 40 | 2012 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 13875 | SF Building | 3.65 | 1.3 | 1 | 1 | 65836.88 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 405 | DX Computer Unit | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | Cooling for the Server Room is provided from a Liebert split DX unit having a cooling capacity of approximately 10 tons. | 2008 | 18 | 2026 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 10 | Each | 3743.74 | 1.3 | 1 | 1 | 48668.62 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 389 | Emergency Eyewash Units and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 25 | 2025 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 5 | Per Lavatory | 7487.48 | 1.3 | 1 | 1 | 48668.62 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 460 | Environmental Chambers | E109002 | Basketball Backboards - Fixed | They building is provided with environmental chambers. | 1998 | 30 | 2028 | 2022 | 2019-11-05 | 3 - Fair | The staff has reported that the electronics have started to fail and are difficult to source. Replacement is recommended. | 10 | Each | 4679.29 | 1.3 | 1 | 1 | 60830.77 | 2 | Active | 992 |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 376 | Epoxy Wall Paint | C301005 | Painted Wall Covering | The building&rsquo;s wall finishes include epoxy paint finish located in the Phytotron, CL3, and, animal lab areas. | 2012 | 10 | 2022 | 2025 | 2019-11-05 | 2 - Good | The wall finish is in good condition overall, no major deficiencies were observed. Life cycle replacement can be deferred. | 12317 | SF Building | 3.65 | 1.3 | 1 | 1 | 58444.17 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 406 | Exhaust System - Fume Hoods - 1972 | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1972 | 25 | 1997 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 16 | Each | 4679.29 | 1.3 | 1 | 1 | 97329.23 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 407 | Exhaust System - Fume Hoods - 1997 | E102007 | Fume Hood Systems | The HVAC ventilation system for the labs includes constant volume fume hood and exhaust systems. | 1997 | 25 | 2022 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 12 | Each | 4679.29 | 1.3 | 1 | 1 | 72996.92 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 380 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with Exit signs to indicate the direction to the means of egress which includes single and double sided LED Exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2012 | 35 | 2047 | 2047 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 3000 | SF | 20.89 | 1.3 | 1 | 1 | 81471 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 410 | Exterior Hollow Metal Door - Double Leaf | B203003 | Exterior - Revolving Doors | The exterior doors consist of hollow metal double-doors mounted by butt hinges to metal door frames. | 1972 | 25 | 1997 | 2026 | 2019-11-05 | 2 - Good | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 1 | Each | 58937.34 | 1.3 | 1 | 1 | 76618.54 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 445 | Exterior Hollow Metal Door - Double Leaf | B203003 | Exterior - Revolving Doors | The exterior doors consist of hollow metal double -doors mounted by butt hinges to metal door frames. | 1994 | 25 | 2019 | 2026 | 2019-11-05 | 2 - Good | The exterior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 1 | Each | 58937.34 | 1.3 | 1 | 1 | 76618.54 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 393 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 11926 | SF Building | 4.58 | 1.3 | 1 | 1 | 71007.4 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 400 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. | 2016 | 20 | 2036 | 2034 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 15403 | SF Building | 4.58 | 1.3 | 1 | 1 | 91709.46 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 422 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 9279 | SF Building | 4.58 | 1.3 | 1 | 1 | 55247.17 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 429 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2016 | 2016 | 20 | 2036 | 2036 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 12454 | SF Building | 4.58 | 1.3 | 1 | 1 | 74151.12 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 451 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building includes a fire alarm system that includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The field devices in this block are connected to the control panel in Block H as a separate zone. | 1994 | 20 | 2014 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 12056 | SF Building | 4.58 | 1.3 | 1 | 1 | 71781.42 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 394 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes a main control panel located in the electrical room, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 11926 | SF Building | 4.58 | 1.3 | 1 | 1 | 71007.4 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 401 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes a main control panel located in the electrical room, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. | 2016 | 20 | 2036 | 2034 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 15403 | SF Building | 4.58 | 1.3 | 1 | 1 | 91709.46 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 423 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system which includes a maim fire alarm control panel, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 9569 | SF Building | 4.58 | 1.3 | 1 | 1 | 56973.83 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 430 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system that includes a main control panel, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 201 | 2016 | 20 | 2036 | 2036 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed . | 12454 | SF Building | 4.58 | 1.3 | 1 | 1 | 74151.12 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 402 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a Fire Alarm System which includes all conduit, wire, and connections to the main control and annunciator panels, pull stations, audio alarm, visual strobes and smoke detectors. | 2016 | 20 | 2036 | 2034 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 15403 | SF Building | 4.58 | 1.3 | 1 | 1 | 91709.46 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 424 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes all conduit, wire, and connections to the main control and annunciator panels, pull stations, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 9279 | SF Building | 4.58 | 1.3 | 1 | 1 | 55247.17 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 431 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes all conduit, wire and connections to the control and annunciation panels, pull stations, audio alarms, visual strobes, smoke detectors and control panels. The system has been updated in 2016. | 2016 | 20 | 2036 | 2036 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 12454 | SF Building | 4.58 | 1.3 | 1 | 1 | 74151.12 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 452 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building includes a fire alarm system that includes all conduit, wire, connections to the main control and annunciator panels, pull stations, audio alarm, visual strobes and smoke detectors. | 1994 | 20 | 2014 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 12056 | SF Building | 4.58 | 1.3 | 1 | 1 | 71781.42 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 384 | Fixed Casework - Lab Benches | C103011 | Millwork General | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1998 | 25 | 2023 | 2033 | 2019-11-05 | 1 - Excellent | The fixed casework is in good condition overall, no significant deficiencies were observed or reported. | 9688 | SF Building | 5.22 | 1.3 | 1 | 1 | 65742.77 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 381 | Foundation Wall and Footings - 10-ft. - Full Basement | A101002 | Low Rise - 1 - 3 Level Building Foundation | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1998 | 75 | 2073 | 2073 | 2019-11-05 | 1 - Excellent | The foundation wall is in good condition overall, no deficiencies were observed. | 29826 | SF Footprint | 23.11 | 1.3 | 1 | 1 | 896062.52 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 385 | Foundation Wall and Footings - 12-ft. - Full Basement | A202002 | Basement Walls | The building is a three -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1972 | 75 | 2047 | 2047 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 5512 | SF Footprint | 34.69 | 1.3 | 1 | 1 | 248574.66 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 433 | Foundation Wall and Footings - 12-ft. - Full Basement | A202002 | Basement Walls | The building is a two -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1982 | 75 | 2057 | 2057 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 3096 | SF Footprint | 34.69 | 1.3 | 1 | 1.5 | 209430.47 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 459 | Fume Hood Exhaust Fans | E102007 | Fume Hood Systems | The laboratories are equipped with Fume Hood exhaust fans and ducting. | 1998 | 25 | 2023 | 2026 | 2019-11-05 | 2 - Good | Not significant deficiencies were observed. Replacement can be deferred. | 10 | Each | 4679.29 | 1.3 | 1 | 1 | 60830.77 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 379 | Hot Water Baseboards | D305004 | Finned Tube Radiation Units | Space heating is provided from perimeter, hot water, baseboard, fin tube, wall convectors and force flow heaters. | 2012 | 30 | 2042 | 2042 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 800 | LF | 80.03 | 1.3 | 1 | 1 | 83231.2 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 387 | Insulated Metal Panel Roof Cover | B301028 | Metal Roofing | The atrium is protected with a prefinished insulated metal standing seam roof cover. | 1972 | 40 | 2012 | 2039 | 2019-11-05 | 1 - Excellent | The roof cover is in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 922 | SF | 24.39 | 1.3 | 1 | 1 | 29233.85 | 1 | Active |  |  |  |  | Operations | South
Planning | 01.053 | 5 | Northrop Auditorium | Saint Paul | 397 | Insulated Metal Panel Roof Cover | B301028 | Metal Roofing | The building's atrium is protected with a corrugated insulated metal standing seam roof cover. | 1972 | 40 | 2012 | 2026 | 2019-11-05 | 2 - Good | The roof cover is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 862 | SF | 24.39 | 1.3 | 1 | 1 | 27331.43 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 426 | Insulated Metal Panel Roof Cover | B301028 | Metal Roofing | The atrium is protected with a prefinished insulated metal standing seam roof cover. | 1972 | 40 | 2012 | 2026 | 2019-11-05 | 2 - Good | The roof cover is in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 691 | SF | 24.39 | 1.3 | 1 | 1 | 21909.54 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 909 | Insulated Metal Panel Roof Cover | B301028 | Metal Roofing | The atrium is protected with a prefinished insulated metal standing seam roof cover. | 2025 | 40 | 2065 | 2065 |  | 1 - Excellent |  | 600 | SF | 24.39 | 1.3 | 1 | 3 | 57072.6 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 917 | Insulated Metal Panel Roof Cover | B301028 | Metal Roofing | The atrium is protected with a prefinished insulated metal standing seam roof cover. | 2025 | 40 | 2065 | 2065 |  | 4 - Poor |  | 800 | SF | 24.39 | 1.3 | 1 | 1 | 25365.6 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 383 | Interior Hollow Metal Swing Doors - Single Leaf - Rated | C102021 | Interior - Single Door - Hollow Metal | The building's interior doors include hollow metal single doors, hinge mounted on metal door frames. | 1998 | 40 | 2038 | 2038 | 2019-11-05 | 1 - Excellent | The building&rsquo;s interior doors are in good condition overall, no deficiencies were observed. | 28 | Each | 2340.03 | 1.3 | 1 | 1 | 85177.09 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 462 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System that includes control panel, arming panels, motion detectors, wiring and conduit. | 2010 | 20 | 2030 | 2030 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 63701 | SF Building | 0.93 | 1.3 | 1 | 1 | 77014.51 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 464 | Metal Panels | B201028 | Insulated Metal Sandwich Panels | The building includes corrugated non insulated wall panels located on the roof. | 1982 | 40 | 2022 | 2026 | 2019-11-05 | 2 - Good | The corrugated metal panels require repainting which will be covered under the maintenance budget. LIfecycle replacement can be deferred. | 1830 | SF | 30.4 | 1.3 | 1 | 1 | 72321.6 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 414 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 1997 | 40 | 2037 | 2037 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 19257 | SF | 1.86 | 1.3 | 1 | 1 | 46563.43 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 438 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 2000 | 40 | 2040 | 2040 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 23896 | SF | 1.86 | 1.3 | 1 | 1 | 57780.53 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 465 | One sided windows | C101005 | Interior Windows | The building&rsquo;s interior windows include one sided monitoring windows located in room 622 and 618. | 2007 | 75 | 2082 | 2057 | 2019-11-05 | 1 - Excellent | The windows are in good condition overall, no deficiencies were observed. | 1055 | SF | 52.22 | 1.3 | 1 | 1 | 71619.73 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 457 | PA System | D503004 | Public Address and Music Systems | The building is provided with a Public Announcement (PA) System which includes amplifier, microphone, speakers and shield wire in conduit. | 1972 | 15 | 1987 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed or reported. Replacement can be deferred. | 35779 | SF Building | 1.86 | 1.3 | 1 | 1 | 86513.62 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 378 | Painted Ceiling | C303006 | Painted Ceiling Structures | The building&rsquo;s ceiling finish include painted GWB ceiling. | 2012 | 15 | 2027 | 2027 | 2019-11-05 | 2 - Good | The ceiling finish is in good condition overall, no major deficiencies were observed. | 26910 | SF | 2.65 | 1.3 | 1 | 1 | 92704.95 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 411 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2010 | 10 | 2020 | 2026 | 2019-11-05 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 19267 | SF Building | 3.65 | 1.3 | 1 | 1 | 91421.92 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 391 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 200 | Each | 293.37 | 1.3 | 1 | 1 | 76276.2 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 398 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 200 | Each | 293.37 | 1.3 | 1 | 1 | 76276.2 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 408 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 200 | Each | 293.37 | 1.3 | 1 | 1 | 76276.2 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 392 | Public Address System | D503004 | Public Address and Music Systems | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2000 | 15 | 2015 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SF Building | 1.86 | 1.3 | 1 | 1 | 86513.62 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 413 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SF Building | 2.65 | 1.3 | 1 | 1 | 66340.37 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 448 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1994 | 50 | 2044 | 2044 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 2.65 | 1.3 | 1 | 1 | 83062.4 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 395 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a Card Access Security System which monitors strategic doors within the facility and consists of controllers, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 70189.35 | 1.3 | 1 | 1 | 91246.16 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 403 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a Card Access System to monitor strategic doors within the facility and includes main control panel, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 70189.35 | 1.3 | 1 | 1 | 91246.16 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 425 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility utilizes a card access security system to monitor strategic doors within the facility and includes controllers, proximity card swipe pads, fob keypads, mag locks and electronic strikes. | 2009 | 15 | 2024 | 2029 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 70189.35 | 1.3 | 1 | 1 | 91246.16 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 432 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a card access security system to monitor strategic doors within the facility and includes controllers, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 70189.35 | 1.3 | 1 | 1 | 91246.16 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 442 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a card access security system which monitors strategic doors within the facility and consists of main control panel, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 70189.35 | 1.3 | 1 | 1 | 91246.16 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 443 | Security System - CCTV | D503008 | Intrusion Alarm Systems | The building is provided with a CCTV security system which monitors points of egress and includes video recorder, monitoring station, cameras, conduit and cabling. | 2010 | 20 | 2030 | 2030 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 68781 | SF Building | 0.93 | 1.3 | 1 | 1 | 83156.23 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 404 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1997 | 20 | 2017 | 2022 | 2019-11-05 | 3 - Fair | The wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 63701 | SF Building | 0.64 | 1.3 | 1 | 1 | 52999.23 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 435 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 1982 | 20 | 2002 | 1997 | 2019-11-05 | 5 - Critical | The building wayfinding signage has aged and is in poor condition, lifecycle replacement is recommended. | 68781 | SF Building | 0.64 | 1.3 | 1 | 1 | 57225.79 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 453 | Signage | C103021 | Standard Fittings and Equipment | The building contains wayfinding signage such as door numbers and signage graphics. | 2007 | 20 | 2027 | 2025 | 2019-11-05 | 2 - Good | The buildings&rsquo;s wayfinding signs are in good condition overall, lifecycle replacement can be deferred. | 89297 | SF Building | 0.64 | 1.3 | 1 | 1 | 74295.1 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 396 | Soffit - Plaster on Metal Lath | B201008 | Exterior Soffits | C-Blocks bridge soffits are prefinished metal panel soffits. | 1972 | 50 | 2022 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed, lifecycle replacement can be deferred. | 6781 | SF | 9.59 | 1.3 | 1 | 1 | 84538.73 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 374 | Standard Foundations | A101003 | Mid Rise - 4 - 8 Level Building Foundation | The building is a five -story structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 2012 | 75 | 2087 | 2087 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed on the exposed superstructure or interior finishes to suggest differential settlement or deterioration of the building foundations. | 9243 | SF Footprint | 50.07 | 1.3 | 1 | 1 | 601636.11 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 382 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade, 6-in. thick. | 1998 | 75 | 2073 | 2073 | 2019-11-05 | 1 - Excellent | The slab on grade is in good condition overall, no deficiencies were observed. | 9052 | SF Footprint | 6.51 | 1.3 | 1 | 1 | 76607.08 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 409 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 7750 | SF Footprint | 6.51 | 1.3 | 1 | 1 | 65588.25 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 444 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1994 | 75 | 2069 | 2069 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 8073 | SF Footprint | 6.51 | 1.3 | 1 | 1 | 68321.8 | 0 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 427 | Terrazzo Flooring - Cast In Place | C302002 | Terrazzo Floor | The building's floor finishes include terrazzo floor finish located in the 200 floor kitchen. | 1972 | 50 | 2022 | 2026 | 2019-11-05 | 2 - Good | The floor finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 1184 | SF | 39.13 | 1.3 | 1 | 1 | 60228.9 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 399 | Transformer - 75 KVA | D501026 | Grounding Methods | The building is equipped with two 75 kVA, 600V - 208Y/120V, 3-Phase, transformers on each floor. | 1972 | 50 | 2022 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 7 | Each | 9358.58 | 1.3 | 1 | 1 | 85163.08 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 421 | Transformers - 45 KVA | D501026 | Grounding Methods | The building is equipped with two 45 KVA, 600V - 208Y/120V transformers on each floor. | 2008 | 50 | 2058 | 2048 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 4 | Each | 9358.58 | 1.3 | 1 | 1 | 48664.62 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 441 | Transformers - 75 KVA | D501026 | Grounding Methods | The electrical system is equipped with 75 KVA, 600V - 208Y/120V transformers on each floor. | 1982 | 50 | 2032 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 7 | Each | 9358.58 | 1.3 | 1 | 1 | 85163.08 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 456 | Unit Heaters | D305002 | Unit Heaters (Hydronic) | The HVAC system is provided with unit heaters. | 2012 | 30 | 2042 | 2039 | 2019-11-05 | 1 - Excellent | No significant deficiencies were observed. | 16 | Each | 2933.7 | 1.3 | 1 | 1 | 61020.96 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 463 | Vinyl sheet | C302006 | Masonry and Stone Floor | The building's floor finishes include sheet vinyl flooring located in D205 computer lab | 2009 | 50 | 2059 | 2026 | 2019-11-05 | 2 - Good | No deficiencies were observed or reported, lifecycle replacement can be deferred. | 1216 | SF | 51.36 | 1.3 | 1 | 1 | 81189.89 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 428 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include asbestos containing vinyl floor tiles located in the laboratories and the corridors. | 1972 | 15 | 1987 | 1987 | 2019-11-05 | 5 - Critical | The vinyl tiles have aged and are in poor condition, lifecycle replacement is recommended. | 5490 | SF | 9.08 | 1.3 | 1 | 1.5 | 97205.94 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 447 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include vinyl tile flooring located in the corridors and labs. | 1994 | 15 | 2009 | 2025 | 2019-11-05 | 2 - Good | The vinyl tiles are in good condition overall, lifecycle replacement can be deferred. | 6028 | SF | 9.08 | 1.3 | 1 | 1 | 71154.51 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 390 | Water Heater - Elec - 43 Litre | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a SpaceSaver, 43-Litre, electric, water heater rated at 3.0 KW. | 2010 | 20 | 2030 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 5615.61 | 1.3 | 1 | 1 | 7300.29 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 437 | Water Heaters | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by three 454 Liters (120-gal), Rheem, electric, water heaters, each rated at 30000 W. | 2010 | 20 | 2030 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 12 | Each | 5615.61 | 1.3 | 1 | 1 | 87603.52 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 416 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems consists of a wet fire standpipe system with backflow protection that Includes distribution piping and shutoff valves. | 1972 | 40 | 2012 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SF Building | 2.43 | 1.3 | 1 | 1 | 60832.86 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 420 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection including distribution piping and shutoff valves | 1972 | 40 | 2012 | 2026 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SF Building | 2.43 | 1.3 | 1 | 1 | 88000.26 | 1 | Active |  |  |  |  | Operations | South
| 01.053 | 5 | Northrop Auditorium | Saint Paul | 450 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection and Includes distribution piping and shutoff valves | 1994 | 40 | 2034 | 2029 | 2019-11-05 | 2 - Good | No significant deficiencies were observed. | 24111 | SF Building | 2.43 | 1.3 | 1 | 1 | 76166.65 | 1 | Active |  |  |  |  | Operations | South
| 31.896 | 6 | Nova Far Detector Building | Orr | 472 | Acid Resistant and Stainless Steel Sinks | D201004 | Sinks | Laboratories contain a mix of acid resistant or stainless steel sinks set in casework. | 2012 | 35 | 2047 | 2025 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. | 104 | Each | 977.9 | 1.3 | 1.18 | 1 | 156010.25 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 477 | Acoustic Tile Ceiling - Exposed T-bar | C303004 | Adhered Acoustic Tile Ceiling | The predominant ceiling finish in the building is suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids. | 1998 | 30 | 2028 | 2026 | 2019-11-04 | 2 - Good | The ceiling tiles are in good condition overall, no deficiencies were observed or reported. Lifecycle replacement can be deferred. | 13993 | SF | 6.15 | 1.3 | 1.18 | 1 | 132011.36 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 528 | Aluminum Screens | C101028 | Interior Guardrails and Screens | Aluminum screens are provided in various places throughout the building. | 2012 | 50 | 2062 | 2062 | 2019-11-04 | 1 - Excellent | The screens are in good condition overall, no major deficiencies were observed. | 276 | LF | 285.39 | 1.3 | 1.18 | 1 | 120829.56 | 0 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 469 | Automatic Door Operators | C102007 | Interior - Automatic Door Openers | The building includes automatic door opening devices located in various locations throughout the building. | 2012 | 15 | 2027 | 2027 | 2019-11-04 | 2 - Good | No major deficiencies were observed or reported. | 20 | Each | 3743.74 | 1.3 | 1.18 | 1 | 114857.94 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 468 | Bridge to Plaza Building | B101002 | Reinforced Concrete Floor | The bridge to the Plaza Building is a steel framed structure with composite steel deck and concrete floor and steel roof deck. Its exterior walls are comprised of four-sided structural silicone curtain wall with insulated glazing units. Its roof is comprised of built-up roofing with black rubberized flood coat and black aggregate surfacing system. It has metal panel soffits. It is finished with porcelain tile flooring and painted ceiling. Replacement costs are for interior finishes and roofing. | 2012 | 75 | 2087 | 2087 | 2019-11-04 | 1 - Excellent | The bridge is in good condition overall, no deficiencies were observed or reported. | 226 | SF Footprint | 77.04 | 1.3 | 1.18 | 4 | 106834.14 | 0 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 529 | Clock System | D503006 | Clock and Program Systems | The building is provided with a centralized automatic wireless clock system which includes single sided clocks and a main controller. | 2012 | 15 | 2027 | 2027 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. | 175990 | SF Building | 0.5 | 1.3 | 1.18 | 1 | 134984.33 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 520 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The building's exterior wall includes split face concrete masonry wall with CMU backup. | 1994 | 75 | 2069 | 2069 | 2019-11-04 | 1 - Excellent | The exterior wall is in fair condition overall, no significant deficiencies were observed or reported. | 1615 | SF | 52.22 | 1.3 | 1.18 | 1 | 129370.35 | 0 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 496 | DDC System | D306006 | Direct Digital Control Systems | HVAC controls include a JOHNSON CONTROLS, DDC control system for system optimization, moderate sensor types and quantities installed throughout the building. | 2010 | 20 | 2030 | 2030 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 31850 | SF Building | 2.79 | 1.3 | 1.18 | 1 | 136313.54 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 497 | DDC/Pneumatic System - Hybrid | D306006 | Direct Digital Control Systems | HVAC controls include a Hybrid DDC /Pneumatic system for system optimization, basic pc control, moderate sensor types with pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 31850 | SF Building | 2.79 | 1.3 | 1.18 | 1 | 136313.54 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 510 | DDC/Pneumatic System - Hybrid - Average | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities including pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SF Building | 2.79 | 1.3 | 1.18 | 1 | 119224.06 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 485 | Distribution Equipment, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal panelboards, feeders, transformers and associated equipment. | 1985 | 40 | 2025 | 2025 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 489 | Distribution Equipment, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal panelboards, feeders, transformers and associated equipment, vertical bus duct, wire and conduit. | 1990 | 40 | 2030 | 2030 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 525 | Distribution Equipment, Panelboards, and Feeders - 600Y/347V & 208Y/120V | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal panelboards, feeders, transformers and associated equipment, as well as vertical bus duct, wire and conduit. | 2007 | 40 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 530 | Distribution Switchboards | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system is provided with distribution switchboards which include incoming feeders, distribution breakers and distribution feeders. | 1972 | 40 | 2012 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 511 | Distribution Switchboards, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal switchboards, panelboards, feeders and associated equipment. | 1990 | 40 | 2030 | 2030 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 516 | Distribution Switchboards, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal power switchboards, panelboards, feeders, transformers, vertical bus duct, wire, conduit and associated equipment. | 1982 | 40 | 2022 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 498 | Distribution Switchboards, Panelboards and Feeders - 1972 | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system for the 1972 section includes essential and normal switchboards, panelboards, feeders, vertical bus duct, wire, conduit and associated equipment. | 1972 | 40 | 2012 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 515 | Distribution Switchboards, Panelboards, and Feeders - 600Y/347V & 208Y/120V | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal switchboards, panelboards, feeders, transformers, vertical bus duct, wire, conduit and associated equipment,. | 1990 | 40 | 2030 | 2030 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 512 | Distribution Switchgear - 15kV, 600A | D501021 | Low Voltage Electrical Service | The electrical distribution system for the building consists of a 15kV, 600A, 3-Phase, 3-bay, switchgear assembly and includes all associated feeds, conduit and wire. | 1997 | 40 | 2037 | 2037 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 27857 | SF Building | 2.79 | 1.3 | 1.18 | 1 | 119224.06 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 522 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; main branch piping, water meter, valves, insulation and fittings. | 1994 | 40 | 2034 | 2034 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 3.65 | 1.3 | 1.18 | 1 | 134999.9 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 508 | Domestic Water Distribution - 1972 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; for main branch piping, water meter, valves, insulation and fittings. | 1972 | 40 | 2012 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 25704 | SF Building | 3.65 | 1.3 | 1.18 | 1 | 143919.27 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 495 | Domestic Water Distribution - 1997 | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; main branch piping, water meter, valves, insulation and fittings. | 1997 | 40 | 2037 | 2037 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 22873 | SF Building | 3.65 | 1.3 | 1.18 | 1 | 128068.21 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 487 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 25 | 1997 | 2026 | 2019-11-04 | 2 - Good | The ceiling finish is in fair condition overall, lifecycle replacement can be deferred. | 11044 | SF | 7.87 | 1.3 | 1.18 | 1 | 133329.57 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 493 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 25 | 1997 | 2026 | 2019-11-04 | 2 - Good | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 11840 | SF | 7.87 | 1.3 | 1.18 | 1 | 142939.35 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 507 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | The building's ceiling finishes include eggcrate ceiling finish located in the offices. | 1972 | 25 | 1997 | 2026 | 2019-11-04 | 2 - Good | The ceiling finish is fair condition overall, lifecycle replacement can be deferred. | 11421 | SF | 7.87 | 1.3 | 1.18 | 1 | 137880.94 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 474 | Emergency Battery Packs and Lights | D509003 | Emergency Lighting Systems | The emergency lighting system includes self-contained battery packs and lights. | 2012 | 20 | 2032 | 2032 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175861 | SF Building | 0.5 | 1.3 | 1.18 | 1 | 134885.39 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 503 | Emergency Eyewash Units and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency eyewash and showers stations installed throughout the building. | 2000 | 25 | 2025 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 12 | Per Lavatory | 7487.48 | 1.3 | 1.18 | 1 | 137829.53 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 481 | Epoxy Flooring | C302007 | Painted / Sealed Floor | The building's floor finishes include cement epoxy floor finish located located in the laboratories on the 400 floor level. | 2000 | 15 | 2015 | 2026 | 2019-11-04 | 2 - Good | The epoxy floor finish is in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 23142 | SF | 3.65 | 1.3 | 1.18 | 1 | 129574.37 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 478 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and includes single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 1998 | 35 | 2033 | 2033 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 4000 | SF | 20.89 | 1.3 | 1.18 | 1 | 128181.04 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 523 | Exterior Storefront Door - Single Leaf | B203028 | Exterior - Double Door - Aluminum and Glass | The exterior doors consist of glazed metal framed single-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 2007 | 35 | 2042 | 2032 | 2019-11-04 | 1 - Excellent | The exterior doors are in good condition overall. | 8 | Each | 8423.03 | 1.3 | 1.18 | 1 | 103367.42 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 499 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building includes a fire alarm system that includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 21237 | SF Building | 4.58 | 1.3 | 1.18 | 1 | 149205.22 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 517 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes pull stations at all exit doors, audio alarms, visual strobes and smoke detectors. | 2014 | 20 | 2034 | 2034 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 22927 | SF Building | 4.58 | 1.3 | 1.18 | 1 | 161078.68 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 500 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system that includes a main control panel, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 21237 | SF Building | 4.58 | 1.3 | 1.18 | 1 | 149205.22 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 518 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes a maim fire alarm control panel, an annunciator panel at the main entrance and a number of secondary control panels throughout the building. The system has been fully upgraded in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 22927 | SF Building | 4.58 | 1.3 | 1.18 | 1 | 161078.68 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 501 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes all conduit, wire, and connections to the control panels, pull stations, audio alarms, visual strobes and smoke detectors. The system has been updated in 2014. | 2014 | 20 | 2034 | 2034 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. Replacement can be deferred. | 21237 | SF Building | 4.58 | 1.3 | 1.18 | 1 | 149205.22 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 519 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes conduit, wire, and connections to the control panel, annunciator panel, pull stations, audio alarms, visual strobes and smoke detectors. | 2014 | 20 | 2034 | 2034 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 22927 | SF Building | 4.58 | 1.3 | 1.18 | 1 | 161078.68 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 486 | Foundation Wall and Footings - 12-ft. - Full Basement | A202002 | Basement Walls | The building is a three -storey structure with a basement. Where exposed, the building foundation walls appear to be poured concrete walls that likely bear on concrete spread footings on either engineered fill or native soil. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 8268 | SF Footprint | 34.69 | 1.3 | 1.18 | 1 | 439977.16 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 482 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include GWB ceiling located in the corridors. | 1972 | 15 | 1987 | 2026 | 2019-11-04 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 37017 | SF | 2.65 | 1.3 | 1.18 | 1 | 150477.81 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 494 | Gypsum Board Ceiling - Fire Resistant | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling finish located in the corridors. | 1972 | 15 | 1987 | 2026 | 2019-11-04 | 2 - Good | The GWB ceiling is in fair condition overall, lifecycle replacement can be deferred. | 39827 | SF | 2.65 | 1.3 | 1.18 | 1 | 161900.74 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 502 | Hollow Metal Single Doors | C102022 | Interior - Single Door - Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1972 | 25 | 1997 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 37 | Each | 2527.14 | 1.3 | 1.18 | 1 | 143435.41 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 492 | Interior Hollow Metal Swing Doors - Double Leaf | C102024 | Interior - Double Door - Hollow Metal | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 1972 | 30 | 2002 | 2026 | 2019-11-04 | 2 - Good | The doors are functioning as intended, lifecycle replacement can be deferred. | 14 | Each | 5615.61 | 1.3 | 1.18 | 1 | 120600.84 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 475 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102024 | Interior - Double Door - Hollow Metal | The building's interior doors include hollow metal double doors, hinge mounted on metal door frames. | 1998 | 30 | 2028 | 2038 | 2019-11-04 | 1 - Excellent | The interior double doors are in good condition overall, no deficiencies were observed. | 16 | Each | 5615.61 | 1.3 | 1.18 | 1 | 137829.53 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 480 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102024 | Interior - Double Door - Hollow Metal | The interior doors include hollow metal double doors with vision panels. | 1972 | 30 | 2002 | 2026 | 2019-11-04 | 2 - Good | The double doors are in good condition overall, and are functioning as intended. Lifecycle replacement can be deferred. | 13 | Each | 5615.61 | 1.3 | 1.18 | 1 | 111986.49 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 491 | Interior Windows - Metal | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 200 floor level. | 1972 | 75 | 2047 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 1884 | SF | 52.22 | 1.3 | 1.18 | 1 | 150918.72 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 488 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes an acid water waste system which consists of glass piping for the laboratories. | 2010 | 30 | 2040 | 2040 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 10764 | SF | 7.3 | 1.3 | 1.18 | 1 | 120537.42 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 531 | Main Distribution Switchboard | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system is provided with a 1000A, 600Y/347V, 3-Phase, 4-Wire, Main Breaker Distribution Switchboard which includes incoming feeder, main breaker, distribution breakers and distribution feeders. | 1972 | 40 | 2012 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 532 | Main Distribution Switchboard | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system for the building is provided with a 3000A, 600V, 3-Phase, 4-Wire, Main Breaker Switchboard which includes incoming feeder, main breaker, distribution feeders and distribution feeders. | 1972 | 40 | 2012 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 526 | Main Distribution Switchboard - 600/347V-1200 A | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system is provided with a 600Y/347V, 3-Phase, 4-Wire, 1200A, Cutler-Hammer, main disconnect switchboard, SWBD-BB, which includes incoming feeder, distribution breakers and distribution feeders. | 2007 | 40 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 97329.54 | 1.3 | 1.18 | 1 | 149303.51 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 471 | Metal Panel Ceiling | C303008 | Linear Metal Panel Ceiling | The building&rsquo;s ceiling finishes include metal panel acoustic ceiling tiles. | 2012 | 30 | 2042 | 2042 | 2019-11-04 | 1 - Excellent | No major deficiencies were observed or reported. | 10118 | SF | 10.87 | 1.3 | 1.18 | 1 | 168713.4 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 483 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 2000 | 40 | 2040 | 2040 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 35779 | SF | 1.86 | 1.3 | 1.18 | 1 | 102086.07 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 476 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB and CMU walls. | 2012 | 10 | 2022 | 2026 | 2019-11-04 | 2 - Good | The painted wall finish is in good condition overall, no major deficiencies were observed. Lifecycle replacement can be deferred. | 25855 | SF Building | 3.65 | 1.3 | 1.18 | 1 | 144764.73 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 506 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2005 | 10 | 2015 | 2026 | 2019-11-04 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 27857 | SF Building | 3.65 | 1.3 | 1.18 | 1 | 155974.13 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 521 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2010 | 10 | 2020 | 2025 | 2019-11-04 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 22991 | SF Building | 3.65 | 1.3 | 1.18 | 1 | 128728.91 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 513 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 level include sections of precast concrete panels. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | The exterior wall system is a fair condition overall, no significant deficiencies were observed. | 1399 | SF | 63.59 | 1.3 | 1.18 | 1 | 136468.34 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 490 | Public Address System | D503004 | Public Address and Music Systems | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2000 | 15 | 2015 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SF Building | 1.86 | 1.3 | 1.18 | 1 | 131876.75 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 509 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SF Building | 2.65 | 1.3 | 1.18 | 1 | 113241.49 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 504 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building is provided with a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SF Building | 4.15 | 1.3 | 1.18 | 1 | 122591.99 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 470 | Sealed Concrete Floor | C302007 | Painted / Sealed Floor | The buildings floor finishes include sealed concrete floor finish located in the mechanical rooms. | 2012 | 15 | 2027 | 2027 | 2019-11-04 | 2 - Good | The sealed concrete floor finish is in poor condition, lifecycle replacement is recommended. | 22581 | SF | 3.65 | 1.3 | 1.18 | 1 | 126433.28 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 527 | Security System - CCTV | D503008 | Intrusion Alarm Systems | The building is provided with a CCTV security system that monitors points of egress and includes video recorder, monitoring station, cameras, conduit and cabling. | 2010 | 20 | 2030 | 2030 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 89297 | SF Building | 0.93 | 1.3 | 1.18 | 1 | 127392.89 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 479 | Structural Slab on Grade | A103001 | Slab on Grade | The building's substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 11324 | SF Footprint | 6.51 | 1.3 | 1.18 | 1 | 113085.31 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 505 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 11421 | SF Footprint | 6.51 | 1.3 | 1.18 | 1 | 114053.99 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 524 | Universal Washrooms | C104022 | Universal / Gender Neutral Washroom Upgrade / Refurbishment | The washrooms are provided with laminated counter tops, painted metal partitions, as well as standard accessories. The washrooms are finished with ceramic floor and wall tiles and painted GWB ceiling finish. The fixtures include floor-mounted water closets and counter top lavatory sinks. | 2007 | 25 | 2032 | 2032 | 2019-11-04 | 1 - Excellent | The washrooms are in good condition overall, no major deficiencies were observed or reported. | 4 | Per Washroom | 23396.45 | 1.3 | 1.18 | 1 | 143560.62 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 473 | Vaccuum Pumps | E102002 | Vacuum Pumps | Vacuum pumps consist of four 7.5HP (40cfm) pumps | 2012 | 20 | 2032 | 2037 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 4 | Each | 18717.16 | 1.3 | 1.18 | 1 | 114848.49 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 484 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet standpipe system with distribution piping and shutoff valves. | 1972 | 40 | 2012 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SF Building | 2.43 | 1.3 | 1.18 | 1 | 133370.52 | 1 | Active |  |  |  |  | Academic | East
| 31.896 | 6 | Nova Far Detector Building | Orr | 514 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with distribution piping and shutoff valves. | 1972 | 40 | 2012 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SF Building | 2.43 | 1.3 | 1.18 | 1 | 141478.09 | 1 | Active |  |  |  |  | Academic | East
| 04.750 | 7 | Science | Mankato | 900 |  | B103002 | Balconies | * Description: (Description &ndash; No drawings &ndash; Concealed) Based on the information gathered during the assessment, the building&rsquo;s overall components are concealed, and a visual site confirmation of the overall building structure or condition was not possible. OR (Description - No drawings - Exposed) At the time of the assessment, where accessible in exposed areas for visual review on site, the building&rsquo;s structural framing system is likely xxxx, xxxx (cast in place concrete columns, beams, and suspended floor and roof slabs/ pre-cast concrete beams, roof, and floor slabs with cast in place concrete columns/ steel columns, beams, and steel open web steel joists OWSJ with corrugated steel deck floors with steel roof beams and steel corrugated roof deck systems/ wood columns, beams, and joist floors/ wood beam and truss roof with wood deck floor and roof sheathing systems). OR (Description - Drawing Confirmation - Cast in Place Concrete Structure) According to the As-Built (or; For Construction/ Tender) drawings provided, the building&rsquo;s overall structure consists of cast in place reinforced concrete columns, beams, and suspended floor and roof slabs (or; supported on steel beams/ trusses/ OWSJ open web steel joists). OR (Description - Masonry Structure) According to the As-Built (or; For Construction/ Tender) drawings provided, the building&rsquo;s overall structure consists of load bearing concrete masonry block units (CMU) (or; load bearing masonry brick/ with steel beams, and steel open web steel joists OWSJ/ with steel trusses/ and corrugated steel deck floors and roof/ wood beams, and joist floors, wood beam and truss roof with a wood deck floor and roof sheathing system). OR (Description - Precast Concrete Structure) According to the As-Built (or; For Construction/ Tender) drawings provided, the building&rsquo;s overall structure consists of pre-cast reinforced concrete deck (or; precast concrete hollow core) sections supported by open web steel joists OWSJ/ steel beams (or; steel trusses/ precast reinforced concrete beams on cast in place reinforced concrete columns and walls/ steel beams). OR (Description - Steel Structure) According to the As-Built (or; For Construction/ Tender) drawings provided, the building&rsquo;s overall structure consists of steel columns, beams, trusses and steel open web steel joists OWSJ with corrugated steel deck and roof floor systems. OR (Description - Wood Structure) According to the As-Built (or; For Construction/ Tender) drawings provided, the building&rsquo;s overall structure consists of wood columns supported on wood load bearing stud walls, beams, and floor joist (or; supported on wood roof trusses/ wood TJIs/ Glulam beams) with wood deck floor and roof sheathing systems. OR (Description - Concrete Post Tensioned Structure) According to the As-Built (or; For Construction/ Tender) drawings provided, the building&rsquo;s overall structure consists of post tensioned reinforced concrete slabs and beams supported by open web steel joists OWSJ and steel beams (or; steel trusses/ steel beams/ cast in place reinforced concrete columns and walls). * Condition Narrative: (Condition - No Observed Deficiencies - Exposed) No major deficiencies were observed or reported on the exposed structural framing system. No significant deterioration was noted or signs to suggest any deterioration or twisting/ movement of the building structure. Replacement has been deferred. OR (Condition - Minor Noted deficiencies - monitor) Some minor deficiencies were observed or reported in the building structural framing system, at the time of assessment which include smaller amounts of xxxx, xxxx, xxxx (concrete spalling /delamination/ step, diagonal, horizontal cracking/ slab/floor deflection/ impact damage/ member twisting/ wood cracking/ splitting etc.) observed in the structure at location xxxx, xxxx, xxxx. While the deficiencies appear to be relatively minor, monitoring is recommended. Should any substantial changes occur, it is recommended that a professional/ experienced structural engineer be retained to analyze the observed changes in deterioration and the effect, if any, on the future performance of the building structure. Repair may be required. OR (Condition - Substantial Noted deficiencies - study) Deficiencies were observed or reported in the building structural framing system, at the time of assessment which include xxxx, xxxx, xxxx (concrete spalling /delamination/ step, diagonal, horizontal cracking/ slab/floor deflection/ impact damage/ member twisting/ wood cracking/ splitting etc.) observed in the structure at location xxxx, xxxx, xxxx. It is recommended that a professional/ experienced structural engineer be retained to analyze the observed deterioration and the effect, if any, on the future performance of the building structure. Replacement/Repair is recommended. OR (Condition - Water staining &ndash; signs of water damage) Staining and/ or signs of water damage such as concrete staining (and; efflorescence/ delamination/ steel corrosion/ rebar corrosion/ water damaged wood) was observed on the building structural systems components located at xxxx, xxxx, xxxx. A study by a professional/ experienced structural engineer is recommended to confirm the extent of the damage/ deterioration and the scope and estimated cost for repair. * Useful Life Narrative: (Useful Life - Elements within expected useful life &ndash; good condition) Based on the conditions observed during the assessment, there was no significant deterioration noted in the overall structure. Based on the current condition, no major repairs or significant improvements to the overall structure are anticipated in the next ten years. OR (Useful Life - Elements nearing or past its expected useful life - No significant deficiencies &ndash; deferred replacement) Based on age, the element has exceeded or will in soon reach its expected useful life. No significant deficiencies were observed or reported. Given the normal service life and the observed condition, the replacement has been deferred beyond the next five years. OR (Useful Life - No significant deficiencies &ndash; cost allowance for partial future repairs/ replacement) Based on age, the element has exceeded or will soon reach its expected useful life. No significant deficiencies were observed or reported. Given the nature of the component, full-scale replacement is not expected to be required. However, a cost allowance for partial replacement/ repair has been carried forward in this report as a precautionary measure. OR (Useful Life - Deficiencies observed &ndash; repair/ replacement) Based on age, the element has exceeded or will soon reach its expected useful life and deficiencies were observed or reported such as xxxx, xxxx, xxxx. Replacement/ Repair is recommended. OR (Useful Life - Specific past deficiencies known &ndash; replacement deferred due to other affected systems) Based on age, the element has exceeded or will soon reach its expected useful life and the reported condition includes a major retrofit of the component within the last five years xxxx, xxxx, xxxx. Replacement has been deferred due to xxx, xxxx, xxxx, (pertinent to mechanical systems.) OR (Useful Life - Deficiencies - Concealed Systems) Based on age, the element has exceeded or will soon reach its expected useful life. The reported condition is consistent with the component age. Due to its concealed nature and critical function, monitoring/ assessments for any changes should be planned, and an engineering study may be required to confirm condition if any signs of deficiencies in performance or deterioration occur. | 1965 | 40 | 2005 | 2024 | 2024-01-24 | 1 - Excellent | System is outdated | 2 | SF | 54.37 | 1.3 | 1.25 | 1 | 176.7 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 537 | Acoustic Tile Ceiling - Exposed T-bar | C303004 | Adhered Acoustic Tile Ceiling | Ceiling finishes located in some offices on the 400 floor level include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2005 | 30 | 2035 | 2030 | 2019-11-07 | 1 - Excellent | The ceiling tiles are in fair condition overall. | 23142 | SF | 6.15 | 1.3 | 1.25 | 1 | 231275.36 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 906 | B301030 - Slate Roofing | B301030 | Slate Roofing | The building has an inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2025 | 50 | 2075 | 2075 |  | 2 - Good |  | 4000 | SF | 30.47 | 1.3 | 1.25 | 1 | 198055 | 0 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 908 | B301031 - Clay Tile Roofing | B301031 | Clay Tile Roofing | The roof is protected with a single-ply ballasted EPDM membrane and rigid insulation board substrate. | 2025 | 50 | 2075 | 2075 |  | 2 - Good |  | 3500 | SF | 30.47 | 1.3 | 1.25 | 1 | 173298.13 | 0 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 597 | C302002 - Terrazzo | C302002 | Terrazzo Floor | The building's floor finish includes asbestos containing vinyl tiles. | 2021 | 50 | 2071 | 2071 | 2019-11-07 | 1 - Excellent |  | 2294 | SF | 39.13 | 1.3 | 1.25 | 1.5 | 218800.29 | 0 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 551 | Carpet Tile Flooring | C302005 | Carpet Floor | The building's floor finishes include carpet tiles located in the offices. | 2005 | 10 | 2015 | 2026 | 2019-11-07 | 2 - Good | The carpet tiles are in fair condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 16146 | SF | 7.87 | 1.3 | 1.25 | 1 | 206487.16 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 540 | Central AHU - 10000 CFM | D304041 | Air Handling Units - Modular - Up to 20,000 CFM | The HVAC system has a central Air Handling Unit with cooling coils and electric heating coils rated 10000 CFM. | 1990 | 30 | 2020 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 127120.84 | 1.3 | 1.25 | 1 | 206571.37 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 541 | Central AHU - 2000 CFM | D304041 | Air Handling Units - Modular - Up to 20,000 CFM | The HVAC system includes a central Air Handling Unit with cooling coils and electric heating coils rated 2000 CFM. | 1984 | 30 | 2014 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 127120.84 | 1.3 | 1.25 | 1 | 206571.37 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 580 | Chilled Water Distribution System | D304006 | Chilled Water Distribution Systems | The HVAC system is provided with a chilled water distribution system which includes distribution piping, valves and insulation. | 1994 | 45 | 2039 | 2039 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 5.51 | 1.3 | 1.25 | 1 | 215883.87 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 542 | DDC/Pneumatic System | D306006 | Direct Digital Control Systems | HVAC controls include a hybrid DDC/Pneumatic system with basic pc control, moderate sensor types and quantities, as well as pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SF Building | 2.79 | 1.3 | 1.25 | 1 | 162213.04 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 548 | DDC/Pneumatic System - Hybrid | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities; and includes pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SF Building | 2.79 | 1.3 | 1.25 | 1 | 209549.93 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 570 | DDC/Pneumatic System - Hybrid | D306006 | Direct Digital Control Systems | HVAC controls consists of a hybrid DDC/Pneumatic system which includes basic pc control, moderate sensor types and quantities, pneumatic activation of control valves and dampers. | 1972 | 20 | 1992 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SF Building | 2.79 | 1.3 | 1.25 | 1 | 172073.95 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 559 | Distribution Equipment - Motor Control Centres | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system for the building includes a motor control centre for the supply and control of electrical power to HVAC equipment and other motor loads and air handing units and includes wire and conduit. | 1972 | 40 | 2012 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 97329.54 | 1.3 | 1.25 | 1 | 158160.5 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 560 | Distribution Switchboards, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system for the building includes essential and normal power switchboards, panelboards, feeders, vertical bus duct, wire, conduit and associated equipment. | 1972 | 40 | 2012 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 97329.54 | 1.3 | 1.25 | 1 | 158160.5 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 581 | Distribution Switchboards, Panelboards and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal power switchboards, panelboards, feeders, transformers, vertical bus duct, wire, conduit and associated equipment. | 1994 | 40 | 2034 | 2034 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 97329.54 | 1.3 | 1.25 | 1 | 158160.5 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 555 | Distribution Switchboards, Panelboards, and Feeders - 1997 | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system for the 1997 section includes essential and normal switchboards, panelboards, feeders, vertical bus duct, wire, conduit and associated equipment. | 1997 | 40 | 2037 | 2037 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 97329.54 | 1.3 | 1.25 | 1 | 158160.5 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 587 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers and VAV terminal boxes with reheat coils installed throughout the building. | 2007 | 50 | 2057 | 2047 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 8296 | SF Building | 10.94 | 1.3 | 1.25 | 1 | 147482.14 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 594 | Elevator - 2 Levels | D101003 | Freight Elevators - Up to 3 Storey | The conveying equipment includes a 510 Kg (1,122 LBS) elevator for 2 levels. | 2012 | 30 | 2042 | 2042 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 133965.37 | 1.3 | 1.25 | 1 | 217693.73 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 596 | Emergency Battery Pack | D509003 | Emergency Lighting Systems | The building is provided with self-contained emergency battery packs and lights. | 2007 | 20 | 2027 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 89297 | SF Building | 0.5 | 1.3 | 1.25 | 3 | 217661.44 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 573 | Emergency Eyewash and Shower Units | D201022 | Universal/Gender Neutral Washroom Fixtures | Plumbing fixtures include emergency safety eyewash and showers stations installed throughout the building. | 2000 | 25 | 2025 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 15 | Per Lavatory | 7487.48 | 1.3 | 1.25 | 1 | 182507.33 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 534 | Emergency Generator - 240kW | D509002 | Emergency Power Generator Systems - Up to 300kVA | The building is equipped with a 300kVA, 240kW, 600V, CATERPILLAR, natural gas, emergency generator which includes batteries, control panel, main breaker and feeder. | 2012 | 30 | 2042 | 2042 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 300 | kVA | 421.19 | 1.3 | 1.25 | 1 | 205330.13 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 593 | Exit Signs | D502022 | Interior Lighting (Industrial) | The building is provided with exit signs to indicate the direction to the means of egress and include single and double sided exit signs, conduit, wire, boxes, conduit bends, connections and circuit breakers. | 2007 | 35 | 2042 | 2042 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 1100 | SF | 20.89 | 1.3 | 1.25 | 5 | 186704.38 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 535 | Exterior Storefront Door - Double Leaf | B203003 | Exterior - Revolving Doors | The exterior doors consist of glass metal framed double-doors mounted by butt hinges to metal door frames. The glass door frames are clear anodized metal and door glazing are insulated glass (IGU). | 1972 | 25 | 1997 | 2022 | 2019-11-07 | 3 - Fair | The exterior doors have aged and exceeded there EUL, lifecycle replacement is recommended. | 2 | Each | 58937.34 | 1.3 | 1.25 | 1 | 191546.36 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 544 | Exterior Storefront Door - Double Leaf | B203003 | Exterior - Revolving Doors | The exterior doors consist of hollow metal glazed double -doors mounted by butt hinges to metal or aluminum door frames. | 1972 | 25 | 1997 | 2022 | 2019-11-07 | 3 - Fair | The exterior doors have aged and are in poor condition, lifecycle replacement is recommended | 2 | Each | 58937.34 | 1.3 | 1.25 | 1 | 191546.36 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 598 | Exterior windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 2024 | 35 | 2059 | 2049 | 2019-11-07 | 1 - Excellent |  | 1210 | SF | 82.62 | 1.3 | 1.25 | 1 | 162451.58 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 589 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes pull stations at all exit doors, audio and visual alarms, smoke detectors and duct smoke detectors. | 2007 | 20 | 2027 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 29762 | SF Building | 4.58 | 1.3 | 1.25 | 1 | 221503.69 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 590 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system which includes a maim control panel in the electrical room, an annunciator panel in the lobby and a number of secondary control panels throughout the building. | 2014 | 20 | 2034 | 2034 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 29762 | SF Building | 4.58 | 1.3 | 1.25 | 1 | 221503.69 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 591 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system which includes all conduit, wire, and connections to the main control panel, secondary panels, pull stations, audible and visual alarms, as well as smoke detectors. | 2007 | 20 | 2027 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 29762 | SF Building | 4.58 | 1.3 | 1.25 | 1 | 221503.69 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 595 | Glazed partitions | C101006 | Glazed Partitions | The building&rsquo;s interior partitions include glazed partitions located in various locations throughout the building. | 2007 | 75 | 2082 | 2057 | 2019-11-07 | 1 - Excellent | The glazed partitions are in good condition overall, no major deficiencies were observed | 1830 | SF | 65.24 | 1.3 | 1.25 | 1 | 194007.45 | 0 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 571 | High Voltage Electrical Service - 15kV, 600A | D501021 | Low Voltage Electrical Service | The electrical distribution system for the building includes a 15kV, 600A, 3-Phase, switchgear assembly that includes incoming feeder and distribution feeders. | 1997 | 40 | 2037 | 2037 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 37954 | SF Building | 2.79 | 1.3 | 1.25 | 1 | 172073.95 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 567 | Hydraulic Freight Elevator | D101003 | Freight Elevators - Up to 3 Storey | The conveying equipment includes a 2-storey hydraulic freight elevator having a capacity of 1814 Kg (4000 lb ). | 2016 | 30 | 2046 | 2046 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 133965.37 | 1.3 | 1.25 | 1 | 217693.73 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 572 | Hydraulic Passenger Elevator - 2-Storey | D101003 | Freight Elevators - Up to 3 Storey | The conveying equipment includes a 2 storey hydraulic passenger elevator with a capacity of 4000LB (1814Kg). | 1982 | 30 | 2012 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 133965.37 | 1.3 | 1.25 | 1 | 217693.73 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 552 | Hydraulic Passenger Elevator - 3-Story | D101003 | Freight Elevators - Up to 3 Storey | The conveying equipment includes a 1588Kg (,500LBS), 3-storey, hydraulic passenger elevator, manufactured by Hydraulic and rated at 40 HP. | 1997 | 30 | 2027 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 133965.37 | 1.3 | 1.25 | 1 | 217693.73 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 577 | Insulated Metal Paneled Walls | B201028 | Insulated Metal Sandwich Panels | The building envelope includes insulated metal panels on steel frame exterior walls. | 1994 | 40 | 2034 | 2034 | 2019-11-07 | 1 - Excellent | The metal panels are in good condition overall, no major deficiencies were observed. | 3272 | SF | 30.4 | 1.3 | 1.25 | 1 | 161636.8 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 545 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102024 | Interior - Double Door - Hollow Metal | The building's interior doors include hollow metal double doors with vision panels, hinge mounted on metal frames. | 1972 | 30 | 2002 | 2026 | 2019-11-07 | 2 - Good | The doors are functioning as intended, lifecycle replacement can be deferred. | 23 | Each | 5615.61 | 1.3 | 1.25 | 1 | 209883.42 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 565 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102024 | Interior - Double Door - Hollow Metal | The interior doors include hollow metal double doors with vision panels. | 1972 | 30 | 2002 | 2026 | 2019-11-07 | 2 - Good | The double doors are in fair condition overall, and are functioning as intended. Lifecycle replacement can be deferred. | 21 | Each | 5615.61 | 1.3 | 1.25 | 1 | 191632.69 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 907 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2025 | 28 | 2053 | 2053 |  | 2 - Good |  | 3616 | SF | 18.74 | 1.3 | 1.25 | 1 | 110116.24 | 0 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 574 | Laboratory Sinks | D201004 | Sinks | The building plumbing fixtures include stainless steel chemical-resistant laboratory sinks. | 1990 | 35 | 2025 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 150 | Each | 977.9 | 1.3 | 1.25 | 1 | 238363.13 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 533 | Mechanical Louvres | B201005 | Exterior Louvers and Screens | The building&rsquo;s exterior wall includes mechanical louvers located at the North-west side of the building. | 2012 | 50 | 2062 | 2052 | 2019-11-07 | 1 - Excellent | No major deficiencies were observed or reported. | 1873 | SF | 60.88 | 1.3 | 1.25 | 1 | 185295.89 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 554 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 1997 | 40 | 2037 | 2037 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 50773 | SF | 1.86 | 1.3 | 1.25 | 1 | 153461.39 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 585 | Painted Ceiling Finish | C303006 | Painted Ceiling Structures | The building's ceiling finishes include painted GWB ceiling. | 2007 | 15 | 2022 | 2025 | 2019-11-07 | 2 - Good | The painted ceiling finish is in good condition overall, no major deficiencies were observed or reported. Lifecycle replacement can be deferred. | 45208 | SF | 2.65 | 1.3 | 1.25 | 1 | 194676.95 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 536 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, and Concrete Masonry walls. | 2010 | 10 | 2020 | 2026 | 2019-11-07 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 37017 | SF Building | 3.65 | 1.3 | 1.25 | 1 | 219557.08 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 566 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, and Concrete Masonry walls. | 2010 | 10 | 2020 | 2026 | 2019-11-07 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 37964 | SF Building | 3.65 | 1.3 | 1.25 | 1 | 225173.98 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 558 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 400 | Each | 293.37 | 1.3 | 1.25 | 1 | 190690.5 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 569 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 400 | Each | 293.37 | 1.3 | 1.25 | 1 | 190690.5 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 576 | Public Address System | D503004 | Public Address and Music Systems | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 2000 | 15 | 2015 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SF Building | 1.86 | 1.3 | 1.25 | 1 | 207890.57 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 539 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage consists of roof drains, interior piping and discharge by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SF Building | 2.65 | 1.3 | 1.25 | 1 | 154073.32 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 547 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SF Building | 2.65 | 1.3 | 1.25 | 1 | 199034.88 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 568 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 37594 | SF Building | 2.65 | 1.3 | 1.25 | 1 | 161889.16 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 562 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron, copper and PVC piping with gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SF Building | 4.15 | 1.3 | 1.25 | 1 | 187860.64 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 579 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1994 | 50 | 2044 | 2044 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 4.15 | 1.3 | 1.25 | 1 | 162598.56 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 553 | Sanitary Waste - Gravity Discharge - 1997 | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1997 | 50 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 22873 | SF Building | 4.15 | 1.3 | 1.25 | 1 | 154249.79 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 556 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility utilizes a card access security system to monitor strategic doors within the facility that includes main control panel, proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 70189.35 | 1.3 | 1.25 | 1 | 114057.69 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 582 | Security System - Card Access | D503001 | Fire Alarm Systems | This facility is provided with a card access security system to monitor strategic doors within the facility that consists of main control panel proximity card swipe pads, keypads, mag locks and electronic strikes. | 2010 | 20 | 2030 | 2030 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 4.58 | 1.3 | 1.25 | 1 | 179446.12 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 592 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility is provided with a card access which includes main control panel, door contacts, proximity card readers, keypads, mag locks, electronic strikes, conduit and wiring. | 2010 | 15 | 2025 | 2030 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 70189.35 | 1.3 | 1.25 | 1 | 228115.39 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 557 | Single-Ply Membrane Roof Cover - Ballasted | B301023 | Conventional - Single Ply Membrane | The roof is protected with a single-ply ballasted EPDM membrane and rigid insulation board substrate. | 2000 | 20 | 2020 | 2026 | 2019-11-07 | 2 - Good | The roof is in fair condition overall, lifecycle replacement can be deferred. | 3454 | SF | 16.1 | 1.3 | 1.25 | 1 | 90365.28 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 584 | Stone Veneer Siding | B201099 | Other Exterior Walls | The exterior walls include areas that have stone veneer siding. | 2007 | 40 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | The exterior wall finish is in good condition overall, no major deficiencies were observed | 25 | Lump Sum | 3850 | 1.3 | 1.25 | 1 | 156406.25 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 543 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 14434 | SF Footprint | 6.51 | 1.3 | 1.25 | 1 | 152693.68 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 564 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 16372 | SF Footprint | 6.51 | 1.3 | 1.25 | 1 | 173195.3 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 583 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade, 6-in. thick.The basement floor is constructed as a concrete slab-on-grade. | 2007 | 75 | 2082 | 2082 | 2019-11-07 | 1 - Excellent | No significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate | 18557 | SF Footprint | 6.51 | 1.3 | 1.25 | 1 | 196309.86 | 0 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 550 | Structural Slab on Grade - 1972 | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1972 | 75 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 18299 | SF Footprint | 6.51 | 1.3 | 1.25 | 1 | 193580.55 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 538 | Traction Passenger Elevator - 3 Floor | D101003 | Freight Elevators - Up to 3 Storey | The conveying equipment includes a three storey, traction geared, elevator rated 907Kg ( 2,000 LBS). | 1972 | 30 | 2002 | 2022 | 2019-11-07 | 3 - Fair | The elevator has been in service 17 years beyond its rated useful life. The staff has reported that spare parts are difficult to obtain. Replacement is recommended. | 1 | Each | 133965.37 | 1.3 | 1.25 | 1 | 217693.73 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 546 | Traction Passenger Elevator - 3 Floor | D101003 | Freight Elevators - Up to 3 Storey | The conveying equipment includes a 3-storey, traction geared, passenger elevator rated 907 Kg (2000LBS). | 1972 | 30 | 2002 | 2022 | 2019-11-07 | 3 - Fair | The elevator has been in service 17 years beyond its rated useful life. The staff has reported that replacement parts are difficult to obtain. Replacement is recommended. | 1 | Each | 133965.37 | 1.3 | 1.25 | 1 | 217693.73 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 561 | Transformer - 1000 KVA | D501026 | Grounding Methods | The building is equipped with a 1000KVA , 13.8kV - 600Y/347V, 3-Phase, transformer located in the Main Electrical Vault. | 2000 | 50 | 2050 | 2040 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 14 | Each | 9358.58 | 1.3 | 1.25 | 1 | 212907.7 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 563 | Transformer - 1000 KVA | D501026 | Grounding Methods | The building is equipped with a 1000 KVA, 13.8kVA - 600Y/347V transformer located in the Main Electrical Vault. | 2000 | 50 | 2050 | 2040 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 14 | Each | 9358.58 | 1.3 | 1.25 | 1 | 212907.7 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 575 | Transformers - 300 KVA & 225 KVA | D501026 | Grounding Methods | The electrical system is equipped with two 300 KVA, 600V - 208Y/120V transformers; and two 225 KVA, 600V - 208Y/120V transformers located in the Main Electrical Vault. | 1982 | 50 | 2032 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 14 | Each | 9358.58 | 1.3 | 1.25 | 1 | 212907.7 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 586 | Water Heater - Elec - 20 Gallon | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 76 Liter (20-gal), John Wood, electric, water heater rated at 1,500 W. | 2012 | 20 | 2032 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 5615.61 | 1.3 | 1.25 | 1 | 9125.37 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 588 | Wet Sprinkler System - 40 HP Fire Pump | D401002 | Sprinklers | The fire protection systems include a 40 HP fire pump and fire pump control panel. | 2007 | 40 | 2047 | 2042 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 22324 | SF Building | 5.01 | 1.3 | 1.25 | 1 | 181745.27 | 1 | Active |  |  |  |  | Academic | South
| 04.750 | 7 | Science | Mankato | 549 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection, distribution piping and shutoff valves. | 1972 | 40 | 2012 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SF Building | 2.43 | 1.3 | 1.25 | 1 | 182511.23 | 1 | Active |  |  |  |  | Academic | South
| 03.521 | 8 | Sports and Health Ctr | Eagan | 623 | Acoustic Tile Ceiling - Exposed T-bar - 1972 | C303004 | Adhered Acoustic Tile Ceiling | The building's ceiling finishes include acoustic ceiling tiles with T-bar suspension system. | 1972 | 30 | 2002 | 2022 | 2019-11-07 | 3 - Fair | The ceiling tiles are in poor condition, lifecycle replacement is recommended. | 25511 | SF | 6.15 | 1.3 | 1.05 | 1 | 214158.47 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 915 | B301030 - Slate Roofing | B301030 | Slate Roofing | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2026 | 50 | 2076 | 2075 |  | 1 - Excellent |  | 10618 | SF | 30.47 | 1.3 | 1.05 | 1 | 441619.08 | 0 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 635 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for the building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SF Building | 8.66 | 1.3 | 1.05 | 1 | 227635.07 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 661 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for this building includes interior and exterior branch wiring, devices, and utilization equipment. | 1994 | 50 | 2044 | 2034 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 8.66 | 1.3 | 1.05 | 1 | 285013.72 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 628 | Branch Wiring - Equipment & Devices - Average Density - 1997 | D502001 | Branch Wiring and Devices | Branch wiring for the 1997 section of the building includes interior and exterior branch wiring, devices and utilization equipment. | 1997 | 50 | 2047 | 2037 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 22873 | SF Building | 8.66 | 1.3 | 1.05 | 1 | 270379.45 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 611 | Ceramic Tile Flooring | C302001 | Ceramic Tile Floor | The building's floor finishes include ceramic floor tiles located in the lobby and the main entrance vestibules. | 1998 | 40 | 2038 | 2028 | 2019-11-07 | 2 - Good | The ceramic tiles are in good condition overall, no significant deficiencies were observed or reported. | 15070 | SF | 15.67 | 1.3 | 1.05 | 1 | 322340.52 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 670 | Chilled Water Piping | D304006 | Chilled Water Distribution Systems | The building is provided with chilled water piping and pumps. | 1972 | 45 | 2017 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SF Building | 5.51 | 1.3 | 1.05 | 1 | 285457.73 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 664 | Chiller - Reciprocating | D303003 | Water Cooled Chillers | Cooling medium is provided by a Trane, reciprocating, air cooled, chiller with a cooling capacity of approximately 140 tons. | 2007 | 30 | 2037 | 2032 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 140 | Ton | 1123.43 | 1.3 | 1.05 | 1 | 214687.47 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 639 | Communal Washroom | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 2005 | 25 | 2030 | 2030 | 2019-11-07 | 1 - Excellent | The washrooms are in fair condition overall. | 6 | Per Lavatory | 23396.45 | 1.3 | 1.05 | 1 | 191616.93 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 617 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish. The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 1972 | 25 | 1997 | 2021 | 2019-11-07 | 4 - Poor | The washrooms have aged and are in poor condition overall, lifecycle replacement is recommended. | 6 | Per Lavatory | 23396.45 | 1.3 | 1.05 | 1 | 191616.93 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 621 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 1972 | 25 | 1997 | 2023 | 2019-11-07 | 3 - Fair | The washrooms have aged and are in poor condition, lifecycle replacement is recommended. | 8 | Per Lavatory | 23396.45 | 1.3 | 1.05 | 1 | 255489.23 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 633 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated countertops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish. The fixtures include floor-mounted water closets, wall-mounted urinals, and countertop lavatory sinks. | 2018 | 25 | 2043 | 2030 | 2019-11-07 | 1 - Excellent | The washrooms are in good condition overall, no significant deficiencies were observed. | 8 | Per Lavatory | 23396.45 | 1.3 | 1.05 | 1 | 255489.23 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 647 | Communal Washrooms | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and counter top lavatory sinks. | 1982 | 25 | 2007 | 2030 | 2019-11-07 | 1 - Excellent | The washrooms have aged and are in poor condition overall, lifecycle replacement is recommended. | 8 | Per Lavatory | 23396.45 | 1.3 | 1.05 | 1 | 255489.23 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 642 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior envelope of the building includes split face concrete masonry walls with CMU back-up. | 1972 | 75 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | The exterior wall is in fair condition overall, no significant deficiencies were observed or reported. | 3767 | SF | 52.22 | 1.3 | 1.05 | 1 | 268512.89 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 609 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) painted concrete masonry walls. | 1998 | 75 | 2073 | 2073 | 2019-11-07 | 1 - Excellent | The CMU partitions are in good condition overall, no deficiencies were observed. | 25855 | SF Building | 8.66 | 1.3 | 1.05 | 1 | 305629.37 | 0 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 631 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | The interior walls are in good condition overall, no significant deficiencies were observed or reported. | 19267 | SF Building | 8.66 | 1.3 | 1.05 | 1 | 227753.28 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 651 | DDC/Pneumatic System - Hybrid | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities with pneumatic activation of control valves and dampers. | 1982 | 20 | 2002 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SF Building | 2.79 | 1.3 | 1.05 | 1 | 261942.12 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 653 | Distribution Switchgears - 15kV, 600A | D501021 | Low Voltage Electrical Service | The electrical distribution system for the building is provided with a 600A,15kV, switchgear which includes fused, 3-Pole, Kirk Inter-locked, interrupter switches and incoming feeder. | 1982 | 40 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SF Building | 2.79 | 1.3 | 1.05 | 1 | 261942.12 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 615 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building is provided with a water distribution system which includes a 4&rdquo; main pipe, water meter, branch piping, valves, insulation and fittings. | 1972 | 40 | 2012 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SF Building | 3.65 | 1.3 | 1.05 | 1 | 178259.92 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 619 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; for main pipe, backflow preventer, distribution piping, water meter, valves, insulation and fittings. | 2014 | 40 | 2054 | 2054 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 46220 | SF Building | 3.65 | 1.3 | 1.05 | 1 | 230279.6 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 644 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; for main branch piping, water meter, valves, insulation and fittings. | 2015 | 40 | 2055 | 2055 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 37594 | SF Building | 3.65 | 1.3 | 1.05 | 1 | 187302.71 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 624 | Domestic Water Distribution - 2015 | D202001 | Domestic Water Piping and Fittings | The building is provided with a water distribution system which includes 4&rdquo; main branch piping, water meter, valves, insulation and fittings. | 2015 | 40 | 2055 | 2055 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 40828 | SF Building | 3.65 | 1.3 | 1.05 | 1 | 203415.3 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 603 | Electric Water Heater - 2012 | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a 27gal, electric, water heater, A.O Smith, model #: DEL 30 110. | 2014 | 20 | 2034 | 2025 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Lifecycle replacement can be deferred. | 1 | Each | 5615.61 | 1.3 | 1.05 | 1 | 7665.31 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 602 | Emergency Eye Wash and Shower Stations | D201011 | Showers (Valve Set) | The plumbing fixtures include Emergency shower and eyewash stations. | 2012 | 25 | 2037 | 2037 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 125 | Each | 1466.85 | 1.3 | 1.05 | 1 | 250281.28 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 604 | Evaporative Coolers | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | The HVAC system is provided with 30HP, rooftop, evaporative coolers | 2012 | 18 | 2030 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 35 | Each | 3743.74 | 1.3 | 1.05 | 1 | 178857.18 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 657 | Exterior Windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1994 | 35 | 2029 | 2026 | 2019-11-07 | 2 - Good | The windows are in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 1722 | SF | 82.62 | 1.3 | 1.05 | 1 | 194200.79 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 606 | Feeders | D501021 | Low Voltage Electrical Service | The electrical system is provided with two 500MCM, 15kV, feeders supplying a double-ended 600A 13.8kV switchgear with tie-breaker. One feeder is from the local municipal hydro, while the other feeder is from the CUB substation. | 2012 | 40 | 2052 | 2052 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 58663 | SF Building | 2.79 | 1.3 | 1.05 | 1 | 223409.24 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 654 | Fixed Casework - Lab Benches | C103011 | Millwork General | Fixed casework in the laboratories includes metal lab benches with acid resistant counter tops. | 1982 | 25 | 2007 | 2022 | 2019-11-07 | 3 - Fair | The fixed casework in the labs are in a very poor condition, lifecycle replacement is recommended. | 44315 | SF Building | 5.22 | 1.3 | 1.05 | 0.66 | 208400.06 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 607 | Fluorescent Fixtures with T8 Lamps | D502002 | Interior Lighting | Fluorescent fixtures with T8 lamps and electronic ballasts are provided in stairwells, service rooms and utility closets, etc. | 2012 | 35 | 2047 | 2042 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 17578 | SF Building | 7.73 | 1.3 | 1.05 | 1 | 185473.39 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 665 | Glazed partitions | C101006 | Glazed Partitions | The building&rsquo;s interior partitions include glazed partitions located on the 4th and 5th floors. | 2012 | 75 | 2087 | 2062 | 2019-11-07 | 1 - Excellent | The glazed partitions are in good condition overall. | 2992 | SF | 65.24 | 1.3 | 1.05 | 1 | 266445.38 | 0 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 610 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1998 | 75 | 2073 | 2073 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 25855 | SF Building | 8.66 | 1.3 | 1.05 | 1 | 305629.37 | 0 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 632 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1972 | 75 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 19267 | SF Building | 8.66 | 1.3 | 1.05 | 1 | 227753.28 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 658 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1994 | 75 | 2069 | 2069 | 2019-11-07 | 1 - Excellent | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 24111 | SF Building | 8.66 | 1.3 | 1.05 | 1 | 285013.72 | 0 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 605 | Heat Recovery Coils | D304025 | Heat Exchangers - Plate and Frame | The HVAC system is provided with Heat recovery coils. | 2012 | 30 | 2042 | 2037 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 4 | Each | 46792.9 | 1.3 | 1.05 | 1 | 255489.23 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 660 | Heating Hot Water Distribution System | D304003 | Heating Water Distribution Systems | The HVAC system is rpovided with a heating hot water distribution system which includes distribution piping, valves and insulation. | 1994 | 45 | 2039 | 2039 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 8.23 | 1.3 | 1.05 | 1 | 270861.77 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 646 | Interior Hollow Metal Swing Doors - Double Leaf - Rated | C102024 | Interior - Double Door - Hollow Metal | The interior doors include hollow metal double doors with vision panels. | 1982 | 30 | 2012 | 2026 | 2019-11-07 | 2 - Good | The interior doors are in a fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 24 | Each | 5615.61 | 1.3 | 1.05 | 1 | 183967.38 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 638 | Interior Hollow Metal Swing Doors - Single Leaf - Rated | C102022 | Interior - Single Door - Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1972 | 25 | 1997 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 75 | Each | 2527.14 | 1.3 | 1.05 | 1 | 258715.96 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 659 | Interior Hollow Metal Swing Doors - Single Leaf - Rated | C102022 | Interior - Single Door - Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1994 | 25 | 2019 | 2034 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed or reported at the time of the field review. | 85 | Each | 2527.14 | 1.3 | 1.05 | 1 | 293211.42 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 663 | Interior Windows - Metal | C101005 | Interior Windows | The building includes windows installed in partition openings. | 2007 | 75 | 2082 | 2057 | 2019-11-07 | 1 - Excellent | The interior windows are in good condition overall, no deficiencies were observed. | 3122 | SF | 52.22 | 1.3 | 1.05 | 1 | 222537.1 | 0 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 666 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System which includes main control panel, motion detectors, arming panels, wiring and conduit. | 2012 | 20 | 2032 | 2032 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 0.93 | 1.3 | 1.05 | 1 | 223410.51 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 608 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building's roof is an inverted roof membrane assembly with a ballasted built-up roof assembly system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2017 | 28 | 2045 | 2045 | 2019-11-07 | 1 - Excellent | The roof is in good condition overall, no major deficiencies were observed or reported. | 9235 | SF | 18.74 | 1.3 | 1.05 | 1 | 236232.22 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 613 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof assembly system, where the built-up roof is insulated and protected by ballast. | 2017 | 28 | 2045 | 2045 | 2019-11-07 | 1 - Excellent | The roof is good condition overall, no deficiencies were observed. | 10473 | SF | 18.74 | 1.3 | 1.05 | 1 | 267900.39 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 634 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes an acid water waste glass piping system for the laboratories. | 2000 | 30 | 2030 | 2030 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 19257 | SF | 7.3 | 1.3 | 1.05 | 1 | 191886.38 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 649 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes an acid waste water glass piping system for the laboratories. | 1984 | 30 | 2014 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 23681 | SF | 7.3 | 1.3 | 1.05 | 1 | 235969.32 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 636 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting system consists of recessed and surface mounted fluorescent fixtures with T-8 lamps and electronic ballasts including conduit and wire. About 25% of the lamps are equipped with emergency power. | 2010 | 35 | 2045 | 2040 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 19257 | SF Building | 7.73 | 1.3 | 1.05 | 1 | 203189.27 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 662 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting system consists of wall mounted and recessed fluorescent fixtures with T- 8 lamps and electronic ballasts, conduit and wire. About 25% of the lamps are equipped with emergency power. | 2005 | 35 | 2040 | 2035 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 7.73 | 1.3 | 1.05 | 1 | 254406.01 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 630 | Metal Wall Louvers | B201005 | Exterior Louvers and Screens | The building's exterior wall includes mechanical metal louvers located on the north side of the building. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 2153 | SF | 60.88 | 1.3 | 1.05 | 1 | 178916.88 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 668 | Motor Control Centres | D501024 | Main Service Panels | The electrical system is provided with motor control centres for the supply and control of electrical power to HVAC equipment and other motor loads. | 2012 | 40 | 2052 | 2052 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 5 | Each | 12166.77 | 1.3 | 1.05 | 3 | 249114.62 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 618 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2010 | 10 | 2020 | 2026 | 2019-11-07 | 2 - Good | The painted wall finish is in good condition overall, no deficiencies were observed. Lifecycle replacement can be deferred. | 46220 | SF Building | 3.65 | 1.3 | 1.05 | 1 | 230279.6 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 622 | Painted Wall Finish | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, CMU and concrete walls. | 2005 | 10 | 2015 | 2026 | 2019-11-07 | 2 - Good | The painted wall finish is in good condition overall. Lifecycle replacement can be deferred. | 63701 | SF Building | 3.65 | 1.3 | 1.05 | 1 | 317374.31 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 650 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating in the washrooms and corridors. | 1982 | 18 | 2000 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50 | Each | 293.37 | 1.3 | 1.05 | 10 | 200225.03 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 656 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 level includes sections of precast concrete panels. | 1994 | 75 | 2069 | 2069 | 2019-11-07 | 1 - Excellent | Efflorescences is observed on the concrete panels. Monitoring is recommended at this time. | 1938 | SF | 63.59 | 1.3 | 1.05 | 1 | 168219.08 | 0 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 601 | Reverse Osmosis Water System | D202023 | Domestic Water Conditioners - Other | The labs are provided with two 60 gpm R.O. water systems. | 2012 | 20 | 2032 | 2032 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 2 | Lump Sum | 7700 | 1.3 | 1.05 | 10 | 210210 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 655 | Roof Construction | B102002 | Reinforced Concrete Roof | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1994 | 75 | 2069 | 2069 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 2454 | SF Footprint | 77.04 | 1.3 | 1.05 | 1 | 258061.66 | 0 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 629 | Roof Deck - Metal Deck on Steel Frame | B102002 | Reinforced Concrete Roof | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1972 | 75 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 2086 | SF Footprint | 77.04 | 1.3 | 1.05 | 1 | 219362.93 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 626 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1997 | 50 | 2047 | 2047 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 63701 | SF Building | 2.65 | 1.3 | 1.05 | 1 | 230422.44 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 648 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1982 | 50 | 2032 | 2032 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 68781 | SF Building | 2.65 | 1.3 | 1.05 | 1 | 248798.07 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 616 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building is provided with a sanitary waste system which consists of cast iron, copper and PVC piping, as well as gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SF Building | 4.15 | 1.3 | 1.05 | 1 | 202679.09 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 620 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building is provided with a sanitary waste system of cast iron, copper and PVC piping with gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SF Building | 4.15 | 1.3 | 1.05 | 1 | 261824.75 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 645 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 37594 | SF Building | 4.15 | 1.3 | 1.05 | 1 | 212960.61 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 625 | Sanitary Waste - Gravity Discharge - 1972 | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes a sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1972 | 50 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40828 | SF Building | 4.15 | 1.3 | 1.05 | 1 | 231280.41 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 643 | SIngle door | C102022 | Interior - Single Door - Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1972 | 25 | 1997 | 2026 | 2019-11-07 | 2 - Good | The interior doors are in fair condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 59 | Each | 2527.14 | 1.3 | 1.05 | 1 | 203523.22 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 600 | Solid Double Doors | C102024 | Interior - Double Door - Hollow Metal | The building includes hollow metal double doors with metal door frames. | 2012 | 30 | 2042 | 2052 | 2019-11-07 | 1 - Excellent | The interior doors are in good condition overall, no major deficiencies were observed. | 30 | Each | 5615.61 | 1.3 | 1.05 | 1 | 229959.23 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 599 | Solid Single Door | C102022 | Interior - Single Door - Wood | The building includes hollow metal and wood single doors attached to metal door frames. | 2012 | 25 | 2037 | 2052 | 2019-11-07 | 1 - Excellent | The single doors are in good condition overall. | 60 | Each | 2527.14 | 1.3 | 1.05 | 1 | 206972.77 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 667 | UPS System | D509007 | UPS Systems | The emergency power system is provided with a 240 kVA, APC, MGE GALAXY, UPS unit. | 2012 | 20 | 2032 | 2032 | 2019-11-07 | 1 - Excellent | No significant deficiencies were observed. | 240 | kVA | 1029.49 | 1.3 | 1.05 | 1 | 337260.92 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 612 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include vinyl floor tiles located in the labs and the hall ways. | 1998 | 15 | 2013 | 2025 | 2019-11-07 | 2 - Good | The vinyl tiles are in a fair condition overall, lifecycle replacement can be deferred. | 17654 | SF | 9.08 | 1.3 | 1.05 | 1 | 218807.21 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 614 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include asbestos containing vinyl floor tiles located in the laboratories and the corridors. | 1972 | 15 | 1987 | 2021 | 2019-11-07 | 4 - Poor | The vinyl tiles have aged significantly and are in poor condition overall. Life cycle replacement is recommended. Cost includes asbestos abatement. | 11926 | SF | 9.08 | 1.3 | 1.05 | 2 | 295626.46 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 640 | Vinyl Tile Flooring - 1972 | C302022 | Vinyl Tile / Plank Floor | The building's floor finish includes asbestos containing vinyl tiles. | 1972 | 15 | 1987 | 2026 | 2019-11-07 | 2 - Good | The vinyl tiles are in fair condition overall, lifecycle replacement can be deferred. | 12317 | SF | 9.08 | 1.3 | 1.05 | 1.5 | 228989.04 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 641 | Water Heater - 2015 - 105 L | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided from a 105 Liter, electric, water heater rated at 1500 W. | 2015 | 20 | 2035 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 5615.61 | 1.3 | 1.05 | 1 | 7665.31 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 669 | Water Heater - Elec- 105 Litres | D202021 | Domestic Water Conditioners - Water Softener Systems | Domestic hot water is provided from a RHEEM, 105-Litre, electric, water heater rated at 6,000 W. | 2015 | 20 | 2035 | 2027 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 5615.61 | 1.3 | 1.05 | 1 | 7665.31 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 627 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a standpipe system which Includes distribution piping, fire hose and shutoff valves | 1972 | 40 | 2012 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 63701 | SF Building | 2.43 | 1.3 | 1.05 | 1 | 211293.03 | 1 | Active |  |  |  |  | Athletics | North
| 03.521 | 8 | Sports and Health Ctr | Eagan | 652 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system which Includes distribution piping and shutoff valves | 1982 | 40 | 2022 | 2026 | 2019-11-07 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SF Building | 2.43 | 1.3 | 1.05 | 1 | 228143.14 | 1 | Active |  |  |  |  | Athletics | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 736 | Acid Resistant Sheet Vinyl | C302006 | Masonry and Stone Floor | The buildings floor finishes include acid resistant sheet vinyl. | 2012 | 50 | 2062 | 2027 | 2019-11-06 | 2 - Good | The floor finish is in good condition overall, no major deficiencies were observed. | 5500 | SF | 51.36 | 1.3 | 1.15 | 1 | 422307.6 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 727 | Acoustic Tile Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | Ceiling finishes located in offices, corridors and bookstore include suspended acoustic tile ceiling assemblies with exposed T-bar suspension system. | 2007 | 25 | 2032 | 2027 | 2019-11-06 | 2 - Good | The acoustic ceiling tiles in a good condition overall, no major deficiencies were observed. | 44089 | SF | 7.87 | 1.3 | 1.15 | 1 | 518735.74 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 674 | Aluminim Doors | C102023 | Interior - Single Door - Aluminum and Glass | The building&rsquo;s interior doors include glazed aluminum framed doors. | 2012 | 35 | 2047 | 2052 | 2019-11-06 | 1 - Excellent | The doors are in good condition overall, no major deficiencies were observed. | 46 | Each | 4679.29 | 1.3 | 1.15 | 1 | 321794.77 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 730 | Boiler HW - Gas-Fired | D302015 | Hot Water Boilers - Over 1000 MBH | Heating hot water is provided by two Viessmann Vitorono 200, gas-fired, hot water boilers, Boiler #1 & Boiler #2, each rated at 2031 MBH. | 2007 | 30 | 2037 | 2037 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 4062 | MBH | 61.6 | 1.3 | 1.15 | 1 | 374077.7 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 688 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 463219.98 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 705 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 360656.22 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 672 | Bridge to MC Building | B101002 | Reinforced Concrete Floor | The bridge to the MC Building is a steel framed structure with composite steel deck and concrete floor and steel roof deck. Its exterior walls are comprised of four-sided structural silicone curtain wall with insulated glazing units, some with fritted glass. Its roof is comprised of standing seam metal paneling. It has metal panel soffits. It is finished with resilient sheet flooring and metal panel ceiling. Replacement costs are for roofing and interior finishes. | 2012 | 75 | 2087 | 2087 | 2019-11-06 | 1 - Excellent | The bridge is in good condition overall, no deficiencies were observed or reported. | 1130 | SF Footprint | 77.04 | 1.3 | 1.15 | 3 | 390442.57 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 703 | Central AHU | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system serving both the C-Block and the F-Block includes a central AHU with chilled water coils, and electric heating elements having a approximate capacity of approximately 20,000 CFM. It branches off into two separate streams and is located in the basement of F-Block. | 1972 | 40 | 2012 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 244462.68 | 1.3 | 1.15 | 1 | 365471.71 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 710 | Central AHU - AHU-1 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system is provided with a 5,000 CFM central AHU that includes chilled water coils, hot water coils and steam humidification. | 1997 | 40 | 2037 | 2037 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 244462.68 | 1.3 | 1.15 | 1 | 365471.71 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 731 | Central AHU - Air Handler - 12000 CFM- AHU-2 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system includes an ENG AIR, Air Handling Unit (AHU-2) with chilled water coils and hot water coils having a capacity of 12,000 CFM. | 2007 | 40 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 244462.68 | 1.3 | 1.15 | 1 | 365471.71 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 718 | Central AHU - Air Handler - 30000 CFM - HC-1 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system has a central AHU with chilled water coils and hot water coils having a approximate capacity of 30000 CFM. | 1985 | 40 | 2025 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. | 1 | Each | 244462.68 | 1.3 | 1.15 | 1 | 365471.71 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 698 | Central AHU - Air Handler - Electric Heat - Serves Both B and E Blocks | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system serving both the B-Block and the E-Block includes a central AHU with chilled water coils, and heating hot water coils having a capacity of approximately 30000 CFM. It branches off into two separate streams and is located in the basement of E-Block. | 1972 | 40 | 2012 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 244462.68 | 1.3 | 1.15 | 1 | 365471.71 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 711 | Central AHU - D and G Blocks | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system includes a 20,000 cfm, central AHU with chilled water coils and electric heating elements that serves both the D-Block and the G-Block. It branches off into two separate streams and is located in the basement of F-Block. | 1972 | 40 | 2012 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1 | Each | 244462.68 | 1.3 | 1.15 | 1 | 365471.71 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 721 | Central Air Handling Unit | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system is provided with a 2,000 cfm, central Air Handling Unit (AHU) that includes chilled water coils, hot water coils and steam humidification. | 1994 | 40 | 2034 | 2034 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 1 | Each | 244462.68 | 1.3 | 1.15 | 1 | 365471.71 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 685 | Communal Washroom | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish. The fixtures include floor-mounted water closets, wall-mounted urinals, and counter top lavatory sinks. | 1972 | 25 | 1997 | 2023 | 2019-11-06 | 3 - Fair | The washrooms have aged and are in poor condition overall, lifecycle replacement is recommended. | 12 | Per Lavatory | 23396.45 | 1.3 | 1.15 | 1 | 419732.31 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 743 | Communal washrooms | C104021 | Communal Washroom Refurbishment | The communal washrooms have standard washroom fixtures and are finished with ceramic floor and wall tiles. The ceiling finish is painted precast ceiling. | 2007 | 25 | 2032 | 2032 | 2019-11-06 | 1 - Excellent | The washrooms are in a good condition overall | 10 | Per Lavatory | 23396.45 | 1.3 | 1.15 | 1 | 349776.93 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 690 | Concrete Masonry Unit Exterior Walls | B201021 | Masonry | The building's exterior wall system include painted concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The exterior walls are in good condition overall, no significant deficiencies were observed or reported. | 5705 | SF | 52.22 | 1.3 | 1.15 | 1 | 445383.07 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 696 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior wall includes split face concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The exterior walls are in a fair condition overall, no significant deficiencies were observed. | 5059 | SF | 52.22 | 1.3 | 1.15 | 1 | 394950.57 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 681 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) painted hollow concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 37017 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 479247.99 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 700 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The interior walls are in good condition overall, no significant deficiencies were observed or reported. | 27857 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 360656.22 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 709 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) painted hollow concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 37964 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 491508.52 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 723 | Copper Clad Siding | B201099 | Other Exterior Walls | The exterior walls include areas that have copper cladding, waterproof membrane, fiberglass sheathed gypsum board, expanded polystyrene insulation, precast concrete panel on structural metal studs. | 2007 | 40 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed or reported. | 70 | Lump Sum | 3850 | 1.3 | 1.15 | 1 | 402902.5 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 927 | D502027 - Pot Light Fixtures | D502027 | Pot Light Fixtures | Pot lights in 2026 | 2025 | 35 | 2060 | 2060 |  | 1 - Excellent |  | 350 | Each | 150.15 | 1.3 | 1.15 | 1 | 78565.99 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 733 | DDC System | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and quantities. | 2007 | 20 | 2027 | 2027 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. | 89297 | SF Building | 2.79 | 1.3 | 1.15 | 1 | 372462.25 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 716 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; for main branch piping, water meter, valves, insulation and fittings. | 1982 | 40 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 61903 | SF Building | 3.65 | 1.3 | 1.15 | 1 | 337789.2 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 699 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system is provided with ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building.. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 19257 | SF Building | 10.94 | 1.3 | 1.15 | 1 | 314954.01 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 722 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal boxes installed throughout the building. | 1994 | 50 | 2044 | 2034 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 24111 | SF Building | 10.94 | 1.3 | 1.15 | 1 | 394342.64 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 694 | Ductwork Distribution System - 1997 | D304001 | Air Distribution Systems | The HVAC system for the1997 section of the building includes ductwork, dampers, diffusers and VAV terminal with hot water reheat coils. | 1997 | 50 | 2047 | 2037 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 22873 | SF Building | 10.94 | 1.3 | 1.15 | 1 | 374094.78 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 686 | Eggcrate Ceiling - Exposed T-bar | C303007 | Suspended Acoustic Ceiling Panels | The building's ceiling finishes include egg crate ceiling tiles located in the offices. | 1972 | 25 | 1997 | 2026 | 2019-11-06 | 2 - Good | The eggcrate ceiling is in good condition overall, no deficiencies were observed. lifecycle replacement can be deferred. | 37017 | SF | 7.87 | 1.3 | 1.15 | 1 | 435529.07 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 719 | Exhaust System - Fume Hoods | D304031 | Exhaust Fans - Centrifugal | The HVAC ventilation system for the labs includes constant volume fume hoods with exhaust systems. | 1990 | 25 | 2015 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 120 | Each | 2808.19 | 1.3 | 1.15 | 1 | 503789.29 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 678 | Exterior windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1998 | 35 | 2033 | 2028 | 2019-11-06 | 2 - Good | The windows are in good condition overall, no significant deficiencies were observed. | 2400 | SF | 82.62 | 1.3 | 1.15 | 1 | 296440.56 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 707 | Exterior Windows | B202001 | Windows | The buildings exterior windows are aluminum framed with insulating glass. | 1972 | 35 | 2007 | 2002 | 2019-11-06 | 5 - Critical | The windows have aged but are in fair condition overall, lifecycle replacement can be deferred. | 3445 | SF | 82.62 | 1.3 | 1.15 | 1 | 425515.72 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 677 | Fume Hoods | E102007 | Fume Hood Systems | The labs are provided with fume hoods, some of which have high-efficiency particulate arrestance or HEPA filters. | 2012 | 25 | 2037 | 2037 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 73 | Each | 4679.29 | 1.3 | 1.15 | 1 | 510674.31 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 682 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's interior partitions include standard gypsum board partitions with painted finish. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The interior partitions are in good condition overall, no significant deficiencies were observed. | 37017 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 479247.99 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 701 | Gypsum Board Partitions - Metal Frame - 1972 | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 27857 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 360656.22 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 742 | Heating Hot Water Piping | D304003 | Heating Water Distribution Systems | The HVAC system is provided with Heating Hot Water piping and pumps. | 1972 | 45 | 2017 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SF Building | 8.23 | 1.3 | 1.15 | 1 | 466980.32 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 684 | Interior Hollow Metal Swing Doors - Single Leaf - Non rated | C102022 | Interior - Single Door - Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 1972 | 25 | 1997 | 2026 | 2019-11-06 | 2 - Good | The interior doors are in good condition overall, no significant deficiencies were observed. Lifecycle replacement can be deferred. | 120 | Each | 2527.14 | 1.3 | 1.15 | 1 | 453368.92 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 683 | Interior Windows - Metal | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 400 floor level. | 1972 | 75 | 2047 | 2026 | 2019-11-06 | 2 - Good | No deficiencies were observed or reported. Lifecycle replacement can be deferred. | 4553 | SF | 52.22 | 1.3 | 1.15 | 1 | 355447.7 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 738 | Intrusion Detection Security System | D503008 | Intrusion Alarm Systems | The building is provided with an Intrusion Detection Security System which consists of main control panel, ultrasonic detection devices, arming panels, conduit and shielded wire. | 2009 | 20 | 2029 | 2029 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. | 269980 | SF Building | 0.93 | 1.3 | 1.15 | 1 | 375366.69 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 691 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2013 | 28 | 2041 | 2041 | 2019-11-06 | 1 - Excellent | The roof is in good condition overall, no significant deficiencies were observed or reported. | 14176 | SF | 18.74 | 1.3 | 1.15 | 1 | 397159.07 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 693 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2016 | 28 | 2044 | 2044 | 2019-11-06 | 1 - Excellent | The roof is in good condition overall, no significant deficiencies were observed or reported. | 16599 | SF | 18.74 | 1.3 | 1.15 | 1 | 465042.56 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 725 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof membrane assembly (IRMA) consisting of ballast, filter fabric, extruded polystyrene insulation board, drainage mat and a fully adhered single-ply membrane | 2007 | 28 | 2035 | 2035 | 2019-11-06 | 1 - Excellent | According to information provided the roof is in good condition overall, no deficiencies were observed. | 9149 | SF | 18.74 | 1.3 | 1.15 | 1 | 256321.13 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 929 | Inverted Roof Membrane Assembly | B301026 | Inverted - Single Ply Membrane | The building has an inverted roof membrane assembly (IRMA) consisting of ballast, filter fabric, extruded polystyrene insulation board, drainage mat and a fully adhered single-ply membrane | 2025 | 28 | 2053 | 2052 |  | 1 - Excellent |  | 9150 | SF | 18.74 | 1.3 | 1.15 | 1 | 256349.15 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 687 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes an acid water waste glass piping system for the laboratories. | 2010 | 30 | 2040 | 2040 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 35779 | SF | 7.3 | 1.3 | 1.15 | 1 | 390474.12 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 702 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes a acid water waste glass piping system for the laboratories. | 2010 | 30 | 2040 | 2040 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 27857 | SF | 7.3 | 1.3 | 1.15 | 1 | 304017.37 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 925 | Lighting - Main and Second Floor | D502002 | Interior Lighting | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts, breakers, conduit and wire. | 2026 | 35 | 2061 | 2059 |  | 1 - Excellent |  | 35779 | SF Building | 7.73 | 1.3 | 1.15 | 1.15 | 475495.84 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 706 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts, breaker, conduit and wire. About 25% of the lamps are equipped with emergency power. | 2009 | 35 | 2044 | 2039 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 27857 | SF Building | 7.73 | 1.3 | 1.15 | 1 | 321925.24 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 926 | Lighting Fixtures - Phase 1 | D502002 | Interior Lighting | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts including conduit and wire. | 2025 | 35 | 2060 | 2059 |  | 1 - Excellent |  | 15000 | SF Building | 7.73 | 1.3 | 1.15 | 1 | 173345.25 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 715 | Painted Wall Finish - Masonry | C301005 | Painted Wall Covering | Standard paint finish is applied to the Concrete Masonry walls. | 2012 | 10 | 2022 | 2022 | 2019-11-06 | 3 - Fair | The painted wall finish is in poor condition, lifecycle replacement is recommended. | 68781 | SF Building | 3.65 | 1.3 | 1.15 | 1 | 375320.72 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 726 | Painted Wall Surface | C301005 | Painted Wall Covering | The building's interior finishes include painted wall finish applied to GWB and CMU partitions. | 2015 | 10 | 2025 | 2025 | 2019-11-06 | 2 - Good | The painted wall finish on the 3rd and 4th floor is in poor condition, repainting is recommended. | 85097 | SF Building | 3.65 | 1.3 | 1.15 | 1 | 464353.05 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 728 | Passenger Elevators | D101004 | Wheelchair Lifts | The conveying equipment includes two 6-storey, 3000 LB (1361 Kg), passenger elevators. | 2007 | 25 | 2032 | 2032 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 12 | Each | 29335.46 | 1.3 | 1.15 | 1 | 526278.15 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 704 | Perimeter Heat - Electric Baseboard | D305010 | Electric Baseboard Heaters | HVAC distribution includes electric baseboard heating around the inside perimeter of the building. | 1972 | 18 | 1990 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 1000 | Each | 293.37 | 1.3 | 1.15 | 1 | 438588.15 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 732 | Perimeter Heat - Electric Baseboard | D305004 | Finned Tube Radiation Units | The HVAC equipment includes electric baseboard heating in the exterior offices. | 2007 | 30 | 2037 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 6000 | LF | 80.03 | 1.3 | 1.15 | 0.5 | 358934.55 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 675 | Porcelain Tile | C302001 | Ceramic Tile Floor | The building&rsquo;s floor finishes include porcelain floor tiles located on the 2nd and 3rd floor corridors. | 2012 | 40 | 2052 | 2042 | 2019-11-06 | 1 - Excellent | The floor tiles are in good condition overall, no major deficiencies were observed. | 18945 | SF | 15.67 | 1.3 | 1.15 | 1 | 443817.88 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 692 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels with concrete masonry unit back-up. | 2005 | 75 | 2080 | 2047 | 2019-11-06 | 1 - Excellent | The precast concrete walls are in fair condition overall, no significant deficiencies were observed or reported. | 3983 | SF | 63.59 | 1.3 | 1.15 | 1 | 378652.06 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 697 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels with concrete masonry unit back-up. | 1972 | 75 | 2047 | 2027 | 2019-11-06 | 4 - Poor | Efflorescence was observed on the precast panels. A study is recommended to investigate the cause with a follow on major repair (based on the results of the study) to correct the issue. | 3337 | SF | 63.59 | 1.3 | 1.15 | 1 | 317238.75 | 2 | Active | 470 |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 673 | Roof Construction | B102002 | Reinforced Concrete Roof | Roof construction Is a reinforced concrete structure supported by CIP concrete columns. | 2012 | 75 | 2087 | 2087 | 2019-11-06 | 1 - Excellent | The roof construction is in good condition overall, no major deficiencies were observed. | 3385 | SF Footprint | 77.04 | 1.3 | 1.15 | 1 | 389866.7 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 680 | Roof Deck - Metal Deck on Steel Frame | B102002 | Reinforced Concrete Roof | The building's roof is a concrete infilled metal pan roof deck on open web steel joists | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The roof deck is in good condition overall, no significant deficiencies were observed or reported. | 3397 | SF Footprint | 77.04 | 1.3 | 1.15 | 1 | 391248.8 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 729 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 2007 | 50 | 2057 | 2057 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 89297 | SF Building | 2.65 | 1.3 | 1.15 | 1 | 353772.39 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 717 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron piping, copper and PVC and gravity discharge to the municipal system. | 1982 | 50 | 2032 | 2032 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 68781 | SF Building | 4.15 | 1.3 | 1.15 | 1 | 426734.52 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 676 | Security System - Card Access & CCTV | D503021 | Audio Visual Systems Theater | The building is provided with a Security system which includes Card readers with electric door strikes and contacts as well as Video surveillance cameras in common areas. | 2012 | 15 | 2027 | 2032 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 4 | Each | 70189.35 | 1.3 | 1.15 | 1 | 419732.31 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 741 | Server room A/C | D303023 | Refrigerant DX Condensing Units - Over 20 Tons | The IT server room is provided with two LIEBERT, 40 ton, DX, A/C units. | 1999 | 18 | 2017 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 8 | Each | 37434.32 | 1.3 | 1.15 | 1 | 447714.47 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 714 | Single door | C102022 | Interior - Single Door - Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either a wood or metal frames. | 1982 | 25 | 2007 | 2022 | 2019-11-06 | 3 - Fair | The interior doors have aged and some doors do not close properly. Lifecycle replacement is recommended. | 107 | Each | 2527.14 | 1.3 | 1.15 | 1 | 404253.95 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 923 | Single-Ply Membrane Roof Cover - Ballasted | B301023 | Conventional - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2024 | 20 | 2044 | 2043 |  | 1 - Excellent |  | 15622 | SF | 16.1 | 1.3 | 1.15 | 1 | 376013.73 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 671 | Slab-on-Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab below grade. The basement floor acts as the slab on grade. | 2012 | 75 | 2087 | 2087 | 2019-11-06 | 1 - Excellent | Where exposed the slab on grade is in good condition overall, no major deficiencies were observed. | 37620 | SF Footprint | 6.51 | 1.3 | 1.15 | 1 | 366134.77 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 713 | Structural Slab on Grade | A103001 | Slab on Grade | The building substructure includes a non-industrial type structural slab on grade. The basement floor is constructed as slab on grade. | 1982 | 75 | 2057 | 2057 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed on the exposed concrete slab-on-grade and no significant deterioration was noted to suggest differential settlement, cracks or deterioration of the concrete slab-on-grade substrate. | 32055 | SF Footprint | 6.51 | 1.3 | 1.15 | 1 | 311973.68 | 0 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 735 | Universal Washroom | C104022 | Universal / Gender Neutral Washroom Upgrade / Refurbishment | The washrooms are provided with standard accessories. The washroom fixtures include floor-mounted water closets and porcelain lavatory sinks. | 2012 | 25 | 2037 | 2037 | 2019-11-06 | 1 - Excellent | The universal washrooms are in good condition overall, no significant deficiencies were observed. | 12 | Per Washroom | 23396.45 | 1.3 | 1.15 | 1 | 419732.31 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 737 | Variable Frequency Drives | D501025 | Main Service Disconnects | The electrical system is provided with variable frequency drives (VFDs) for the control of motor speeds. | 2012 | 40 | 2052 | 2032 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 30 | Each | 9358.58 | 1.3 | 1.15 | 1 | 419732.31 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 720 | Water Heater - 50 Gal | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 189 L (50 gal), Rheem, electric, water heater rated at 9000 W. | 2000 | 20 | 2020 | 2025 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5615.61 | 1.3 | 1.15 | 1 | 16790.67 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 679 | Water Heater - Elec - Residential - 40 Gallon | D202021 | Domestic Water Conditioners - Water Softener Systems | The domestic hot water is provided by a 151 Liter (40-gallon), electric, water heater rated at 3000 W | 2010 | 20 | 2030 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5615.61 | 1.3 | 1.15 | 1 | 16790.67 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 739 | Water Tank Heater - 2005 | D202021 | Domestic Water Conditioners - Water Softener Systems | The water distribution system is provided with a RHEEM, 175 Liter (46 gal), electric, water tank heater. | 2005 | 20 | 2025 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 2 | Each | 5615.61 | 1.3 | 1.15 | 1 | 16790.67 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 740 | Water Tank Heater - 2011 | D202021 | Domestic Water Conditioners - Water Softener Systems | The water distribution system is provided with a JOHN WOOD, 184 Liter (48 gal), electric, water tank heater. | 2011 | 20 | 2031 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred | 2 | Each | 5615.61 | 1.3 | 1.15 | 1 | 16790.67 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 695 | Wet Sprinkler System | D401002 | Sprinklers | The fire protection system for the 1997 section of Block D consists of a wet sprinkler system that includes backflow prevention, distribution piping, spare sprinkler heads, fire department hose connections and shutoff valves. | 1997 | 40 | 2037 | 2032 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 63701 | SF Building | 5.01 | 1.3 | 1.15 | 1 | 477117.3 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 734 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection, distribution piping and shutoff valves | 2007 | 40 | 2047 | 2042 | 2019-11-06 | 1 - Excellent | No significant deficiencies observed. | 89297 | SF Building | 2.43 | 1.3 | 1.15 | 1 | 324402.61 | 1 | Active |  |  |  |  | Operations | North
| 22.054 | 9 | The Oswald Visitor Center | Miami | 724 | Window walls | B202003 | Window Walls | The exterior envelope of the building includes areas of window wall system with insulating glass. The window walls include operable units. | 2007 | 40 | 2047 | 2057 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 2691 | SF | 108.73 | 1.3 | 1.15 | 1 | 437425.68 | 0 | Active |  |  |  |  | Operations | North
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 804 | Acoustic Panel Ceiling - Perforated Metal Panel | C303008 | Linear Metal Panel Ceiling | The building's ceiling finishes include suspended perforated metal panel ceiling with concealed suspension system. | 2007 | 30 | 2037 | 2037 | 2019-11-06 | 1 - Excellent | The suspended ceiling tiles are in good condition overall, no major deficiencies were observed. | 36597 | SF | 10.87 | 1.3 | 1.15 | 1 | 594725.04 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 782 | Acoustic Tile Ceiling - Exposed T-bar - 1997 | C303004 | Adhered Acoustic Tile Ceiling | The building's ceiling finishes include acoustic ceiling tiles with T-bar suspension system. | 1997 | 30 | 2027 | 2026 | 2019-11-06 | 2 - Good | The ceiling tiles are in good condition overall, lifecycle replacement can be deferred. | 79653 | SF | 6.15 | 1.3 | 1.15 | 1 | 732349.6 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 746 | Acoustical Ceiling Tiles | C303004 | Adhered Acoustic Tile Ceiling | The building&rsquo;s ceiling finishes include suspended acoustic ceiling tile (ACT) system with regular tiles in suspended prefinished metal grids. | 2012 | 30 | 2042 | 2037 | 2019-11-06 | 1 - Excellent | The ceiling finish ACT tiles are in good condition overall, no deficiencies were observed. | 75993 | SF | 6.15 | 1.3 | 1.15 | 1 | 698698.64 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 774 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 598396.47 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 792 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 491379.05 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 785 | Branch Wiring - Equipment & Devices - Average Density - 1972 | D502001 | Branch Wiring and Devices | Branch wiring for the 1972 section of the building includes interior and exterior branch wiring, devices and utilization equipment. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40828 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 528587.87 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 813 | Cabinets - Millwork | C103009 | Fixed Casework | Millwork includes wall and under counter cabinets and plastic laminate countertops without appliances located in the offices and Labs. | 2012 | 35 | 2047 | 2042 | 2019-11-06 | 1 - Excellent | The millwork is in good condition overall, no major deficiencies were observed. | 919 | LF | 428.09 | 1.3 | 1.15 | 1 | 588154.99 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 807 | Central AHU - Air Handler - 8000 CFM- AHU-1, AHU-4 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system includes two ENG AIR, Air Handling Units (AHU-1 & AHU-4) with chilled water coils and hot water coils. AHU-1, 7300 cfm AHU-4, 7960 cfm | 2007 | 40 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 244462.68 | 1.3 | 1.15 | 1 | 730943.41 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 808 | Central AHU - Air Handler - 9600 CFM- AHU-3, AHU-5 | D304042 | Air Handling Units - Built- Up - Over 20,000 CFM | The HVAC system includes two ENG AIR, Air Handling Units (AHU-3 & AHU-5) with chilled water coils and hot water coils, each having a capacity of 9600 CFM. | 2007 | 40 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 2 | Each | 244462.68 | 1.3 | 1.15 | 1 | 730943.41 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 802 | Ceramic Tile Wall Surface | C301023 | Ceramic Wall Tile | The interior wall finishes include ceramic tile wall finish located at the main entrance. | 2007 | 40 | 2047 | 2037 | 2019-11-06 | 1 - Excellent | The ceramic wall finish is in good condition overall. | 37674 | SF | 13.95 | 1.3 | 1.15 | 1 | 785700.69 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 797 | Chilled Water - Building Chilled Water Distribution System | D304006 | Chilled Water Distribution Systems | The chilled water piping system includes distribution piping, valves and insulation, installed in the mechanical rooms for chilled water to the air handlers. | 1985 | 45 | 2030 | 2030 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 68781 | SF Building | 5.51 | 1.3 | 1.15 | 1 | 566580.05 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 809 | Chilled Water Distribution System | D304006 | Chilled Water Distribution Systems | The HVAC system is provided with a chilled water distribution system which includes distribution piping, valves and insulation that provides chilled water to the air handlers. | 2007 | 45 | 2052 | 2052 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 89297 | SF Building | 5.51 | 1.3 | 1.15 | 1 | 735579.57 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 752 | Chiller CH-01 | D303003 | Water Cooled Chillers | Chilled water is provided from a 297.7 ton, McQuay, Model #: WSC063-DAABM, chiller, CRN-CH-01, with R134A, refrigerant, coupled with two evaporative fluid coolers located on the rooftop. It was reported that CH-01 provides chilled water for process cooling load in the labs. | 2012 | 30 | 2042 | 2037 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 300 | Ton | 1123.43 | 1.3 | 1.15 | 1 | 503858.36 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 790 | Communal Washroom | C104021 | Communal Washroom Refurbishment | The washrooms are provided with laminated counter tops, painted metal floor-mounted partitions, as well as standard accessories. The washrooms are finished terrazzo floor finish, painted, concrete masonry walls, and ACT ceiling finish.The fixtures include floor-mounted water closets, wall-mounted urinals, and counter top lavatory sinks. | 2005 | 25 | 2030 | 2030 | 2019-11-06 | 1 - Excellent | The washrooms are in fair condition overall, no significant deficiencies were observed. | 14 | Per Lavatory | 23396.45 | 1.3 | 1.15 | 1 | 489687.7 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 812 | Communal Washroom | C104021 | Communal Washroom Refurbishment | The washrooms are provided with painted metal floor-mounted partitions, as well as standard accessories. The washroom fixtures include floor-mounted water closets, wall-mounted urinals, and porcelain lavatories. | 2012 | 25 | 2037 | 2037 | 2019-11-06 | 1 - Excellent | The washrooms are in good condition overall, no significant deficiencies were observed. | 20 | Per Lavatory | 23396.45 | 1.3 | 1.15 | 1 | 699553.86 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 767 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior envelope of the stairwells is 8" split-rib concrete masonry unit construction. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The split face concrete masonry unit is in fair condition overall, no significant deficiencies were observed or reported. | 8396 | SF | 52.22 | 1.3 | 1.15 | 1 | 655466.48 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 777 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior wall includes split face concrete masonry unit with CMU backup | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The exterior wall is in fair condition overall, no significant deficiencies were observed. | 6674 | SF | 52.22 | 1.3 | 1.15 | 1 | 521031.84 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 769 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The interior walls are in good condition overall, no significant deficiencies were observed or reported. | 46220 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 598396.47 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 779 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) concrete masonry walls. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The interior walls are in good condition overall, no significant deficiencies were observed or reported. | 63701 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 824717.74 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 795 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) painted hollow concrete masonry walls. | 1982 | 75 | 2057 | 2057 | 2019-11-06 | 1 - Excellent | The interior partitions are in good condition overall, no deficiencies were observed. | 68781 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 890486.97 | 0 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 751 | Condensing Boilers | D302015 | Hot Water Boilers - Over 1000 MBH | Heating hot water is provided from two 2,500MBH, CLEAVER BROOKS, Model: CFC-700-2500-125-HW, condensing boilers. | 2012 | 30 | 2042 | 2042 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 5000 | MBH | 61.6 | 1.3 | 1.15 | 1 | 460460 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 753 | Cooling Towers | D303021 | Refrigerant DX Condensing Units - Up to 5 Tons | The HVAC equipment is provided with four 300 ton, roof-mounted, galvanized, cooling towers. | 2012 | 18 | 2030 | 2037 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 80 | Each | 3743.74 | 1.3 | 1.15 | 1 | 447751.3 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 754 | DDC System | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system compatible with Johnson Metasys for system optimization, pc control, with moderate sensor types and quantities. | 2012 | 20 | 2032 | 2032 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 175861 | SF Building | 2.79 | 1.3 | 1.15 | 1 | 733525.02 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 814 | Distribution Paneboards | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system for this building includes distribution panelboards, feeders and associated equipment. | 2012 | 40 | 2052 | 2052 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 5 | Each | 97329.54 | 1.3 | 1.15 | 1 | 727538.31 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 818 | Distribution Switchboards | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system is provided with distribution switchboards. | 2012 | 40 | 2052 | 2052 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 5 | Each | 97329.54 | 1.3 | 1.15 | 1 | 727538.31 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 805 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; for main branch pipe, distribution piping, backflow preventer, water meter, valves, insulation and fittings. | 2007 | 40 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 89297 | SF Building | 3.65 | 1.3 | 1.15 | 1 | 487271.4 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 765 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35779 | SF Building | 10.94 | 1.3 | 1.15 | 1 | 585176.28 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 789 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 27857 | SF Building | 10.94 | 1.3 | 1.15 | 1 | 455609.59 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 791 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 37954 | SF Building | 10.94 | 1.3 | 1.15 | 1 | 620749.06 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 784 | Ductwork Distribution System - 1972 | D304001 | Air Distribution Systems | The HVAC system for the 1972 section of the building includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 40828 | SF Building | 10.94 | 1.3 | 1.15 | 1 | 667754.19 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 747 | Elevators - 5 Levels | D101003 | Freight Elevators - Up to 3 Storey | The building contains two KONE traction elevators, #1 & #3, both rated 2,206 Kg (5000LBS) which serve 5 floors of the building; and one elevator, #2, which serves the 100 and 200 levels of the building. The elevator cab finishes consist of stainless steel doors, door returns, and walls with textured rubber flooring. | 2012 | 30 | 2042 | 2037 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 3 | Each | 133965.37 | 1.3 | 1.15 | 1 | 600834.68 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 768 | Exterior windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1972 | 35 | 2007 | 2022 | 2019-11-06 | 3 - Fair | The windows have aged and have broken seals. Lifecycle replacement is recommended. | 5274 | SF | 82.62 | 1.3 | 1.15 | 1 | 651428.13 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 760 | Fire Alarm System - Activation and Notification Devices | D503001 | Fire Alarm Systems | This building is provided with a fire alarm system that includes pull stations at all exit doors, audio devices, visual devices and smoke detectors. | 1998 | 20 | 2018 | 2025 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 89986 | SF Building | 4.58 | 1.3 | 1.15 | 1 | 616143.14 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 761 | Fire Alarm System - Control Panels | D503001 | Fire Alarm Systems | This building is equipped with a fire alarm system that includes a maim fire alarm control panel and a number of secondary control panels throughout the building. | 2014 | 20 | 2034 | 2034 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 89986 | SF Building | 4.58 | 1.3 | 1.15 | 1 | 616143.14 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 762 | Fire Alarm System - Wiring | D503001 | Fire Alarm Systems | This building includes a fire alarm system that includes all conduit, wire, and connections to the main control panel, pull stations audio/visual strobes, smoke detectors and control panels. | 1998 | 20 | 2018 | 2025 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 89986 | SF Building | 4.58 | 1.3 | 1.15 | 1 | 616143.14 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 748 | Gas-Fired Water Heater | D202031 | Domestic Water Heat Exchangers | Domestic hot water is provided from three 1,000MBH, semi-instantaneous, gas fired, water heaters, each with 1116gph recovery that includes recirculation pump and 552gal storage tank. | 2012 | 30 | 2042 | 2027 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. | 50 | Each | 7487.48 | 1.3 | 1.15 | 1 | 559689.13 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 770 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 46220 | SF Building | 8.66 | 1.3 | 1.15 | 1 | 598396.47 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 798 | Heating Hot Water - Building Hot Water Distribution System | D304003 | Heating Water Distribution Systems | The building heating hot water distribution system includes distribution piping, valves and insulation. | 1985 | 45 | 2030 | 2030 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 68781 | SF Building | 8.23 | 1.3 | 1.15 | 1 | 846271.11 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 819 | HHW Piping | D304003 | Heating Water Distribution Systems | The HVAC system is provided with heating hot water (HHW) piping, valves and pumps. | 1972 | 45 | 2017 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 63701 | SF Building | 8.23 | 1.3 | 1.15 | 1 | 783767.55 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 815 | High Voltage Electrical Service | D501021 | Low Voltage Electrical Service | The building is provided with a 13.8kV, 600A main electrical service switchgear. | 2012 | 40 | 2052 | 2052 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 2.79 | 1.3 | 1.15 | 1 | 734063.09 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 772 | Interior Hollow Metal Swing Doors - Single Leaf - Nonrated | C102022 | Interior - Single Door - Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on either wood or metal frames. | 1972 | 25 | 1997 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review, lifecycle replacement can be deferred. | 135 | Each | 2527.14 | 1.3 | 1.15 | 1 | 510040.03 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 771 | Interior Windows - Metal | C101005 | Interior Windows | The building includes window units and storefront windows installed in partition openings located on the 400 and 300 floors. | 1972 | 75 | 2047 | 2026 | 2019-11-06 | 2 - Good | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. Lifecycle replacement can be deferred. | 10010 | SF | 52.22 | 1.3 | 1.15 | 1 | 781469.69 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 794 | Inverted Roof Membrane Assembly | B301023 | Conventional - Single Ply Membrane | The building's roof has a inverted roof membrane system, where the roof membrane is a single-ply built-up roof membrane protected by gravel. | 2010 | 20 | 2030 | 2030 | 2019-11-06 | 1 - Excellent | The roof is good condition overall, no deficiencies were observed. | 30105 | SF | 16.1 | 1.3 | 1.15 | 1 | 724612.3 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 783 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes a acid water waste glass piping system for the laboratories. | 1972 | 30 | 2002 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 50773 | SF | 7.3 | 1.3 | 1.15 | 1 | 554111.14 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 775 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting system consists of surface and recessed mounted fluorescent fixtures with T-8 lamps and electronic ballasts, conduit and wire. | 2000 | 35 | 2035 | 2030 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 46220 | SF Building | 7.73 | 1.3 | 1.15 | 1 | 534134.5 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 786 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting system consists of recessed and surface mounted fluorescent fixtures with T-8 lamps and electronic ballasts including conduit and wire . | 2000 | 35 | 2035 | 2030 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 63701 | SF Building | 7.73 | 1.3 | 1.15 | 1 | 736151.05 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 800 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting system consists of recessed and surface mounted fluorescent fixtures with T- 8 lamps, conduit and wire. About 25% of the lamps are equipped with emergency power. | 2005 | 35 | 2040 | 2035 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 68781 | SF Building | 7.73 | 1.3 | 1.15 | 1 | 794857.31 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 817 | Lightning Protection System | D509004 | Lightning Protection Systems | The electrical system is provided with a lightning protection system. | 2012 | 50 | 2062 | 2062 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 2.29 | 1.3 | 1.15 | 1 | 602510.56 | 0 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 756 | Main Distribution Switchboard | D501022 | Main Service Switchboards - 800A to 1600A | The electrical system is provided with a 3,000A, 600Y/347V, 3-Phase, 4-Wire, double ended, SQUARE D, main breaker, distribution switchboard with tie breaker. | 2012 | 40 | 2052 | 2052 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 5 | Each | 97329.54 | 1.3 | 1.15 | 1 | 727538.31 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 820 | Main Electrical System Transformer | D501026 | Grounding Methods | The electrical system for the building is provided with a 2500 kVA, 13.8kV - 600Y/347V, main transformer. | 1972 | 50 | 2022 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 35 | Each | 9358.58 | 1.3 | 1.15 | 1 | 489687.7 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 758 | Natural Gas Distribution for Lab | D301002 | Natural Gas Supply Piping and Fittings | The building includes a natural gas distribution system for the laboratories. | 1998 | 40 | 2038 | 2038 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 161459 | SF | 1.86 | 1.3 | 1.15 | 1 | 448969.04 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 750 | Natural Gas Supply | D301002 | Natural Gas Supply Piping and Fittings | The building is provided with a natural gas piping system and supply from the local utility. | 2012 | 40 | 2052 | 2052 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 175861 | SF | 1.86 | 1.3 | 1.15 | 1 | 489016.68 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 745 | Paint | C301005 | Painted Wall Covering | Standard paint finish is applied to the GWB, and concrete walls. | 2012 | 10 | 2022 | 2025 | 2019-11-06 | 2 - Good | The painted wall finish is in good condition overall, lifecycle replacement can be deferred. | 168173 | SF Building | 3.65 | 1.3 | 1.15 | 1 | 917678.02 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 757 | Pendant Fixtures | D502002 | Interior Lighting | The dining areas and the central 200-300 level open corridors are provided with decorative pendant mounted fixtures which are tied into a Lutron lighting control system that consists of lighting schedules, as well as passive infrared and ultrasonic occupancy sensors. Selected fixtures contain emergency battery backup ballasts to provide egress lighting in the event of an outage. | 2012 | 35 | 2047 | 2042 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 58663 | SF Building | 7.73 | 1.3 | 1.15 | 1 | 677930.16 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 810 | Perimeter Heat System - Hydronic Fin Tube | D305004 | Finned Tube Radiation Units | The HVAC equipment includes a two-pipe system of heating hot water with hydronic fin tube perimeter units. | 2007 | 30 | 2037 | 2037 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 6000 | LF | 80.03 | 1.3 | 1.15 | 1 | 717869.1 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 744 | Phytotron Skylight | B302021 | Skylights | Aluminum-framed phytotron skylight with vertical insulated glazing units and slope single-glazing units. | 2012 | 25 | 2037 | 2037 | 2019-11-06 | 1 - Excellent | The phytotron skylight is continuously leaking due to a design deficiency. Repairs to the system are currently ongoing between the University and building (in litigation). | 3445 | SF | 136.27 | 1.3 | 1.15 | 1 | 701827.97 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 764 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | The exterior wall system is in a fair condition overall, no significant deficiencies were observed. | 5167 | SF | 63.59 | 1.3 | 1.15 | 1 | 491211.45 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 788 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels with concrete masonry unit back-up. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed or reported. | 7427 | SF | 63.59 | 1.3 | 1.15 | 1 | 706062.98 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 759 | Public Address System | D503004 | Public Address and Music Systems | The building is provided with a public address system which includes amplifiers, speakers, conduit and shielded wiring. | 1998 | 15 | 2013 | 2025 | 2019-11-06 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 269980 | SF Building | 1.86 | 1.3 | 1.15 | 1 | 750733.39 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 749 | Rainwater Drainage | D204001 | Rain Water Drainage Piping and Fittings | The building is provided with a rain water drainage includes interior piping, roof drains and pumped discharge to the municipal main. | 2012 | 50 | 2062 | 2062 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 175861 | SF Building | 2.65 | 1.3 | 1.15 | 1 | 696717.32 | 0 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 801 | Roof Deck - Concrete on Permanent Steel Form On Steel Frame | B102002 | Reinforced Concrete Roof | The 5th floor mechanical penthouse roof deck is a concrete infilled metal pan deck on open web steel joists. No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 2007 | 75 | 2082 | 2082 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed or reported. | 5570 | SF Footprint | 77.04 | 1.3 | 1.15 | 1 | 641523.64 | 0 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 766 | Roof Deck - Metal Deck on Steel Frame | B102002 | Reinforced Concrete Roof | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 4330 | SF Footprint | 77.04 | 1.3 | 1.15 | 1 | 498706.88 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 776 | Roof Deck - Metal Deck on Steel Frame | B102002 | Reinforced Concrete Roof | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1972 | 75 | 2047 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 5489 | SF Footprint | 77.04 | 1.3 | 1.15 | 1 | 632194.48 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 787 | Roof Deck - Metal Deck on Steel Frame | B102002 | Reinforced Concrete Roof | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1972 | 75 | 2047 | 2030 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed on the exposed roof deck to suggest movement of the building structure. Also no significant deficiencies were observed on the exposed superstructure to suggest deterioration or movement of the building structure. | 3426 | SF Footprint | 77.04 | 1.3 | 1.15 | 1.2 | 473506.64 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 806 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron piping, copper and PVC with gravity discharge to the municipal system. | 2007 | 50 | 2057 | 2057 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 89297 | SF Building | 4.15 | 1.3 | 1.15 | 1 | 554020.91 | 0 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 763 | Security System - Card Access | D503021 | Audio Visual Systems Theater | This facility utilizes a card access security system to monitor strategic doors within the facility which consists of controllers, swipe and proximity card readers, keypads, mag locks and electronic strikes. | 2010 | 15 | 2025 | 2030 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 6 | Each | 70189.35 | 1.3 | 1.15 | 1 | 629598.47 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 803 | Sheet Vinyl Goods Flooring | C302006 | Masonry and Stone Floor | Floor finishes located in the classrooms on the 400 and 300 floor levels include areas of sheet vinyl flooring and related base. | 2007 | 50 | 2057 | 2025 | 2019-11-06 | 2 - Good | The sheet vinyl floor finish is in good condition overall, lifecycle replacement can be deferred. | 9053 | SF | 51.36 | 1.3 | 1.15 | 1 | 695118.31 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 780 | Single door | C102022 | Interior - Single Door - Wood | The building's interior doors are either solid wood doors or hollow metal doors, hinge mounted on metal frames. | 1972 | 25 | 1997 | 2026 | 2019-11-06 | 2 - Good | No significant deficiencies were observed or reported at the time of the field review. Lifecycle replacement can be deferred. | 165 | Each | 2527.14 | 1.3 | 1.15 | 1 | 623382.26 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 793 | Split Face Concrete Masonry Unit | B201021 | Masonry | The building's exterior wall include sections of concrete masonry unit. | 1982 | 75 | 2057 | 2057 | 2019-11-06 | 1 - Excellent | The exterior wall is in fair condition overall, no significant deficiencies were observed or reported. | 6523 | SF | 52.22 | 1.3 | 1.15 | 1 | 509243.43 | 0 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 755 | Standpipes | D402001 | Standpipes | The building is equipped with a standpipe system with approximately 6 fire hose cabinets located on each floor. The standpipe system is supplied by a 25HP, 500GPM fire pump located in Mechanical room 162. | 2012 | 40 | 2052 | 2047 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 2.43 | 1.3 | 1.15 | 1 | 639345.27 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 816 | Steam Distribution System | D304002 | Steam Distribution Systems | The HVAC system includes a steam distribution piping and pump system including condensate return tank with pumps. | 2012 | 45 | 2057 | 2057 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 10.01 | 1.3 | 1.15 | 0.3 | 790104.47 | 0 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 799 | Transformer - 1250 KVA | D501026 | Grounding Methods | The main electrical service isprovided with 1250 KVA, 15 kV - 600Y/347V transformers located in the Main Electrical Vault. | 1982 | 50 | 2032 | 2048 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 45 | Each | 9358.58 | 1.3 | 1.15 | 1 | 629598.47 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 773 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Plank Floor | The building's floor finish includes asbestos containing vinyl tiles. | 1972 | 15 | 1987 | 1987 | 2019-11-06 | 5 - Critical | The floor tiles have exceeded their EUL and are in a poor condition overall, lifecycle replacement is recommended. Costing includes abatement of asbestos. | 43926 | SF | 9.08 | 1.3 | 1.15 | 1.5 | 894416.82 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 796 | Vinyl Tile Flooring | C302022 | Vinyl Tile / Plank Floor | The building's floor finishes include asbestos containing vinyl floor tiles located in the laboratories and the corridors. | 1982 | 15 | 1997 | 1997 | 2019-11-06 | 5 - Critical | The vinyl tiles have aged significantly and are in very poor condition overall, life cycle replacement is recommended. Note that cost includes abatement of asbestos. | 29315 | SF | 9.08 | 1.3 | 1.15 | 2 | 795878.8 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 781 | Vinyl Tile Flooring - 1972 | C302022 | Vinyl Tile / Plank Floor | The building's floor finish includes asbestos containing vinyl tiles located in the corridors and labs. | 1972 | 15 | 1987 | 2021 | 2019-11-06 | 4 - Poor | The vinyl tiles are in poor condition overall, lifecycle replacement is recommended. Note that costing includes asbestos abatement. | 24757 | SF | 9.08 | 1.3 | 1.15 | 2 | 672132.74 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 811 | Wet Sprinkler System - Piping | D401002 | Sprinklers | The fire protection systems include a wet sprinkler system with backflow preventer, distribution piping, shutoff valves, fire department hose connections and spare sprinkler heads. | 2007 | 40 | 2047 | 2042 | 2019-11-06 | 1 - Excellent | No significant deficiencies were observed. | 89297 | SF Building | 5.01 | 1.3 | 1.15 | 1 | 668830.07 | 1 | Active |  |  |  |  | Academic | West
| 05.891 | 10 | University Teaching and Outreach Ctr | Brainerd | 778 | Window Wall - 2005 | B202003 | Window Walls | The buildings fenestration includes custom aluminum framed sash with insulating glass. | 2005 | 40 | 2045 | 2037 | 2019-11-06 | 1 - Excellent | The windows are in good condition overall, no significant deficiencies. | 3660 | SF | 108.73 | 1.3 | 1.15 | 1 | 594937.94 | 1 | Active |  |  |  |  | Academic | West
| 01.204 | 11 | Wilson Library | Cottage Grove | 893 | Acid Waste System | D209002 | Acid Waste Systems | The labs are provided with an acid waste system. | 2012 | 30 | 2042 | 2042 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF | 7.3 | 1.3 | 1 | 1 | 1670145.1 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 834 | Air Handling Units | D304041 | Air Handling Units - Modular - Up to 20,000 CFM | The HVAC system includes nine AHUs (From 4,300 to 38,000 CFM), "Haakon Industries", Model #: AIRPAK. AHU-1, 30,600 cfm, serving labs on 500 Level; AHUs-3a and 3b, 4,300 cfm each, serving CL3 lab on 500 Level; AHU-4, 37,976 cfm, serving labs on 400 Level; AHU-5, 22,000 cfm, serving offices and hallways on 400 and 500 Levels; AHU-6, 38,000 cfm, serving offices and hallways on 300, 200 and 100 Levels; AHU-7, 17,500 cfm, serving labs on 300, 200 and 100 Levels; AHUs-8a and 8b, 23,000 cfm each, serving Comparative Bioscience Facility Spaces (animal labs). | 2012 | 30 | 2042 | 2042 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 9 | Each | 127120.84 | 1.3 | 1 | 1 | 1487313.83 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 822 | Aluminum Wall Screen | B201028 | Insulated Metal Sandwich Panels | Prefinished aluminum hexagonal wall screen on south elevation with two metal grating catwalks. | 2012 | 40 | 2052 | 2052 | 2019-11-04 | 1 - Excellent | The hexagonal wall screen is in good condition overall, no major deficiencies were observed. | 22529 | SF | 30.4 | 1.3 | 1 | 1 | 890346.08 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 838 | Branch Wiring | D502001 | Branch Wiring and Devices | Branch wiring for this building includes a concentration of branch wiring, devices and utilization equipment. | 2012 | 50 | 2062 | 2052 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175861 | SF Building | 8.66 | 1.3 | 1 | 1 | 1979843.14 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 854 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1998 | 50 | 2048 | 2038 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 8.66 | 1.3 | 1 | 1 | 3039434.84 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 881 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 1982 | 50 | 2032 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SF Building | 8.66 | 1.3 | 1 | 1 | 774336.5 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 887 | Branch Wiring - Equipment & Devices | D502001 | Branch Wiring and Devices | Branch wiring for this building includes interior and exterior branch wiring, devices and utilization equipment. | 2007 | 50 | 2057 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies observed. | 89297 | SF Building | 8.66 | 1.3 | 1 | 1 | 1005305.63 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 847 | Chilled Water - Building Chilled Water Distribution System | D304006 | Chilled Water Distribution Systems | The building chilled water distribution system includes distribution piping, valves and insulation, installed throughout the building. | 1998 | 45 | 2043 | 2043 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 5.51 | 1.3 | 1 | 1 | 1933866.74 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 894 | Chilled Water Distribution System | D304006 | Chilled Water Distribution Systems | The HVAC system is provided with a chilled water distribution system. | 2012 | 45 | 2057 | 2057 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 5.51 | 1.3 | 1 | 1 | 1260616.37 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 833 | Chillers CH-02 and CH-03 | D303003 | Water Cooled Chillers | Chilled water is provided from two 750 ton, McQuay, Model #: C3012BNYY2-A, chillers, CRN-CH-02 & CRN-CH-03, coupled with four open circuit rooftop cooling towers. | 2012 | 30 | 2042 | 2037 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 1500 | Ton | 1123.43 | 1.3 | 1 | 1 | 2190688.5 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 889 | CMU partitions | C101001 | Fixed Partitions | The buildings interior partitions include concrete masonry partitions located at the loading dock area. | 2012 | 75 | 2087 | 2087 | 2019-11-04 | 1 - Excellent | The concrete masonry partitions are in good condition&rsquo;s overall, no major deficiencies were observed. | 176173 | SF Building | 8.66 | 1.3 | 1 | 1 | 1983355.63 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 872 | Concrete Masonry Unit Exterior Walls - Split Rib | B201021 | Masonry | The exterior wall includes split face concrete masonry unit with CMU backup. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | The exterior wall is in fair condition overall, no significant deficiencies were observed. | 14531 | SF | 52.22 | 1.3 | 1 | 1 | 986451.47 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 883 | Concrete Masonry Unit Partitions | C101001 | Fixed Partitions | The building's interior partitions include 150 MM (6-in) hollow concrete block located in the back area of the bookstore. | 2007 | 75 | 2082 | 2082 | 2019-11-04 | 1 - Excellent | The concrete masonry partition is in good condition overall. | 89297 | SF Building | 8.66 | 1.3 | 1 | 1 | 1005305.63 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 826 | Conventional BUR | B301021 | Conventional - Built-Up Roof | The flat roof structure has a conventional roof assembly system, where the roof membrane is a multi-ply built-up roof membrane protected by a white flood coat and white aggregate surfacing system. Gravel stops completed with pre-finished metal cap flashing are provided at the roof perimeter. | 2012 | 22 | 2034 | 2034 | 2019-11-04 | 1 - Excellent | The roof is in good condition overall, no roof leaks were reported or observed. | 36120 | SF | 17.45 | 1.3 | 1 | 1 | 819382.2 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 896 | Curtain wall | B202003 | Window Walls | The building includes a curtain wall system with vision and spandrels panels form the building exterior wall system. | 2007 | 40 | 2047 | 2057 | 2019-11-04 | 1 - Excellent | The curtain wall system is in good condition overall, no significant deficiencies were observed or reported. | 12325 | SF | 108.73 | 1.3 | 1 | 1 | 1742126.43 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 824 | Curtain Wall - Acid Etched Glazing Units | B202003 | Window Walls | 4-sided structural silicone curtain wall with insulated acid-etched glazing units at the phytotron. | 2012 | 40 | 2052 | 2062 | 2019-11-04 | 1 - Excellent | The system is in good condition overall, no deficiencies were observed. | 43841 | SF | 108.73 | 1.3 | 1 | 1 | 6196881.51 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 823 | Curtain Walls | B202003 | Window Walls | 4-sided structural silicone curtain wall with insulated fritted glazing units cover most of the building. Parallel opening operable units are located in offices on the south elevation. | 2012 | 40 | 2052 | 2062 | 2019-11-04 | 1 - Excellent | The curtain walls are leaking constantly due to poor design, on-going legal matters with the supplier to resolve the problem. | 43841 | SF | 108.73 | 1.3 | 1 | 1 | 6196881.51 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 851 | DDC/Pneumatic System - Hybrid - Average | D306006 | Direct Digital Control Systems | HVAC controls include a DDC system for system optimization, basic pc control, moderate sensor types and pneumatic activation of control valves and dampers with DDC interface. | 2005 | 20 | 2025 | 2025 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. | 269980 | SF Building | 2.79 | 1.3 | 1 | 1 | 979217.46 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 853 | Distribution Equipment, Panelboards, and Feeders | D501022 | Main Service Switchboards - 800A to 1600A | The electrical distribution system includes essential and normal panelboards, feeders and associated equipment, vertical bus duct, wire and conduit. | 1998 | 40 | 2038 | 2038 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 6 | Each | 97329.54 | 1.3 | 1 | 1 | 759170.41 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 843 | Domestic Water Distribution | D202001 | Domestic Water Piping and Fittings | The building water distribution system includes a 4&rdquo; for main branch pipe, distribution piping, water meter, valves, insulation and fittings. | 1998 | 40 | 2038 | 2038 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 3.65 | 1.3 | 1 | 1 | 1281055.1 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 829 | Domestic Water System | D202001 | Domestic Water Piping and Fittings | The building is provided with a domestic water system which includes a 4-inch main line, water meter and rpz backflow preventer. | 2012 | 40 | 2052 | 2052 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 3.65 | 1.3 | 1 | 1 | 835072.55 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 836 | Dry Type Transformers | D501026 | Grounding Methods | The electrical system is provided with two 2,500 kVA, 13.8 kV - 600Y/347V, HPS, transformers. | 2012 | 50 | 2062 | 2052 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 75 | Each | 9358.58 | 1.3 | 1 | 1 | 912461.55 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 848 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, VAV terminal boxes installed throughout the building. | 1998 | 50 | 2048 | 2038 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 10.94 | 1.3 | 1 | 1 | 3839655.56 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 862 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal with electric reheat coils and actuator/controls installed throughout the building. | 1972 | 50 | 2022 | 2026 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. Replacement can be deferred. | 46220 | SF Building | 10.94 | 1.3 | 1 | 1 | 657340.84 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 880 | Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system includes ductwork, dampers, diffusers, CAV terminal boxes installed throughout the building. | 1982 | 50 | 2032 | 2055 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. Replacement can be deferred. | 68781 | SF Building | 10.94 | 1.3 | 1 | 1 | 978203.38 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 837 | Emergency Generator - 1040kW | D509002 | Emergency Power Generator Systems - Up to 300kVA | The emergency power system is provided with a 1300kVA, 1040kW, 600V CATERPILLAR, natural gas, emergency generator which includes batteries, control panel, main breaker and feeder; as well as an ASCO 7000, Automatic Transfer Switches, ATS-1 rated 100A, 600V; ATS-2 rated 800A, 600V; and ATS-3 rated 800A, 600V. | 2012 | 30 | 2042 | 2042 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 3065 | kVA | 421.19 | 1.3 | 1 | 1.01 | 1695013.87 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 858 | Exterior windows | B202001 | Windows | The buildings exterior windows are aluminum framed with insulating glass. | 1972 | 35 | 2007 | 2022 | 2019-11-04 | 3 - Fair | The windows have aged and have broken seals, lifecycle replacement is recommended. | 8396 | SF | 82.62 | 1.3 | 1 | 1 | 901780.78 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 865 | Exterior windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1972 | 35 | 2007 | 2026 | 2019-11-04 | 2 - Good | The windows have aged but are in fair condition overall, lifecycle replacement can be deferred. | 34445 | SF | 82.62 | 1.3 | 1 | 1 | 3699599.67 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 869 | Exterior Windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1972 | 35 | 2007 | 2026 | 2019-11-04 | 2 - Good | The windows have aged but are in fair condition overall, lifecycle replacement can be deferred. | 35521 | SF | 82.62 | 1.3 | 1 | 1 | 3815168.53 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 873 | Exterior windows | B202001 | Windows | The buildings exterior windows include custom aluminum framed sash with insulating glass. | 1972 | 35 | 2007 | 2026 | 2019-11-04 | 2 - Good | The windows have aged but are in fair condition overall, lifecycle replacement can be deferred. | 11814 | SF | 82.62 | 1.3 | 1 | 1 | 1268894.48 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 840 | Fire Alarm System | D503001 | Fire Alarm Systems | The building is provided with a Fire Alarm System which includes a main control panel, pull stations at exit doors, audible and visual alarms, duct smoke detectors, smoke & heat detectors. | 2012 | 20 | 2032 | 2032 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175861 | SF Building | 4.58 | 1.3 | 1 | 1 | 1047076.39 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 856 | Fireproofing - Fiber Encasement | B101002 | Reinforced Concrete Floor | 1-hour fire resistance rated sprayed on fiber encasement fireproofing for structural components. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No deficiencies were observed. | 12955 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 1297469.16 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 859 | Fireproofing - Fiber Encasement | B101002 | Reinforced Concrete Floor | The building includes 1-hour fire resistance rated sprayed on fiber encasement fireproofing for structural components. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 16177 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 1620158.9 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 863 | Fireproofing - Fiber Encasement | B101002 | Reinforced Concrete Floor | 1-hour fire resistance rated sprayed on fiber encasement fireproofing for structural components. | 1972 | 75 | 2047 | 2072 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 22295 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 2232888.84 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 867 | Fireproofing - Fiber Encasement | B101002 | Reinforced Concrete Floor | 1-hour fire resistance rated sprayed on fiber encasement fireproofing for structural components. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 6743 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 675324.94 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 870 | Fireproofing - Fiber Encasement | B101002 | Reinforced Concrete Floor | The building includes 1-hour fire resistance rated sprayed on fiber encasement fireproofing for structural components. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 9749 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 976381.85 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 874 | Fireproofing - Fiber Encasement | B101002 | Reinforced Concrete Floor | 1-hour fire resistance rated sprayed on fiber encasement fireproofing for structural components. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No deficiencies were observed. | 13287 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 1330719.62 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 877 | Fireproofing - Fiber Encasement | B101002 | Reinforced Concrete Floor | 1-hour fire resistance rated sprayed on fiber encasement fireproofing for structural components. | 1982 | 75 | 2057 | 2057 | 2019-11-04 | 1 - Excellent | No deficiencies were observed. | 24073 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 2410959.1 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 821 | Floor Construction | B101002 | Reinforced Concrete Floor | The building consists of a multi-story concrete structure and includes concrete columns, beams, floor slabs, and roof structure. | 2012 | 75 | 2087 | 2087 | 2019-11-04 | 1 - Excellent | The floor construction is in good condition overall, no deficiencies were observed. | 61660 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 6175372.32 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 895 | Floor Construction | B101002 | Reinforced Concrete Floor | The suspended floors are concrete infilled metal pan decks on open web steel joists | 1994 | 75 | 2069 | 2073 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 8438 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 845082.58 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 857 | Floor Deck - Concrete on Permanent Steel Form On Steel Frame | B101002 | Reinforced Concrete Floor | The suspended floors are a concrete infilled metal pan decks on open web steel joists. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 12955 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 1297469.16 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 860 | Floor Deck - Concrete on Permanent Steel Form On Steel Frame | B101002 | Reinforced Concrete Floor | The suspended floors are concrete infilled metal pan decks on open web steel joists | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 16177 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 1620158.9 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 864 | Floor Deck - Concrete on Permanent Steel Form On Steel Frame | B101002 | Reinforced Concrete Floor | The suspended floors are concrete infilled metal pan decks on open web steel joists | 1972 | 75 | 2047 | 2072 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 22295 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 2232888.84 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 868 | Floor Deck - Concrete on Permanent Steel Form On Steel Frame | B101002 | Reinforced Concrete Floor | The suspended floors are concrete infilled metal pan decks on open web steel joists | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 6743 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 675324.94 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 871 | Floor Deck - Concrete on Permanent Steel Form On Steel Frame | B101002 | Reinforced Concrete Floor | The suspended floors are concrete infilled metal pan decks on open web steel joists | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 9749 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 976381.85 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 875 | Floor Deck - Concrete on Permanent Steel Form On Steel Frame | B101002 | Reinforced Concrete Floor | The suspended floors are concrete infilled metal pan decks on open web steel joists. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 13287 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 1330719.62 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 878 | Floor Deck - Concrete on Permanent Steel Form On Steel Frame | B101002 | Reinforced Concrete Floor | The suspended floors are a concrete infilled metal pan decks on open web steel joists. | 1982 | 75 | 2057 | 2057 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 24073 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 2410959.1 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 882 | Floor Deck - Concrete Plank - Hollow Core | B101002 | Reinforced Concrete Floor | The building&rsquo;s floor construction is of precast hollow core plank on steel beams. | 2007 | 75 | 2082 | 2082 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 31253 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 3130050.46 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 839 | Fluorescent Fixtures with T5 Lamps | D502002 | Interior Lighting | The interior lighting system includes 1&rsquo; x 4&rsquo; recessed fluorescent fixtures with T5 lamps and electronic ballasts in offices and laboratories. Lighting control is provided by a Lutron lighting control system that consists of lighting schedules, as well as passive infrared and ultrasonic occupancy sensors. | 2012 | 35 | 2047 | 2042 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 100158 | SF Building | 7.73 | 1.3 | 1 | 1 | 1006487.74 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 890 | Glycol Distribution System | D304005 | Glycol Distribution Systems | The HVAC system is provided with a Glycol distribution system. | 2012 | 45 | 2057 | 2057 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF | 8.23 | 1.3 | 1 | 1 | 1882917.01 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 827 | GWB Partitions | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 2012 | 75 | 2087 | 2087 | 2019-11-04 | 1 - Excellent | The interior partitions are in good condition overall. | 176173 | SF Building | 8.66 | 1.3 | 1 | 1 | 1983355.63 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 884 | Gypsum Board Partitions - Metal Frame | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 2007 | 75 | 2082 | 2082 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 89297 | SF Building | 8.66 | 1.3 | 1 | 1 | 1005305.63 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 866 | Gypsum Board Partitions - Metal Frame - 1972 | C101001 | Fixed Partitions | The building's fixed partitions appear to be metal framed stud walls completed with drywall. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | The interior partitions are in good condition overall, no significant deficiencies were observed or reported. | 96875 | SF Building | 8.66 | 1.3 | 1 | 1 | 1090618.75 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 849 | Heating Hot Water - Building Hot Water Distribution System | D304003 | Heating Water Distribution Systems | The heating hot water (HHW) distribution system includes distribution piping, valves and insulation, installed in mechanical rooms and throughout the building. | 1998 | 45 | 2043 | 2043 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 8.23 | 1.3 | 1 | 1 | 2888516.02 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 886 | Heating Hot Water Distribution System | D304003 | Heating Water Distribution Systems | The heating hot water distribution system includes distribution piping, valves, insulation and circulation pumps installed in the 5th floor mechanical penthouse. | 2007 | 45 | 2052 | 2052 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 89297 | SF Building | 8.23 | 1.3 | 1 | 1 | 955388.6 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 892 | Heating Hot Water Distribution System | D304003 | Heating Water Distribution Systems | The HVAC system is provided with a heating hot water distribution system. | 2012 | 45 | 2057 | 2057 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 8.23 | 1.3 | 1 | 1 | 1882917.01 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 891 | HVAC Ductwork Distribution System | D304001 | Air Distribution Systems | The HVAC system is provided with distribution ductwork, diffusers and plenum return installed throughout the building. | 2012 | 50 | 2062 | 2052 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175990 | SF Building | 10.94 | 1.3 | 1 | 1 | 2502929.78 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 846 | Lab Acid Waste System - Glass Pipe | D209002 | Acid Waste Systems | The building includes a glass piped acid water waste piping system for the laboratories. | 1998 | 30 | 2028 | 2028 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. | 161459 | SF | 7.3 | 1.3 | 1 | 1 | 1532245.91 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 855 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting consists of surface mounted fluorescent 1&rsquo; X 4&rsquo; fixtures with T- 8 lamps and electronic ballasts, conduit and wire. About 25% of the lamps are equipped with emergency power. | 2005 | 35 | 2040 | 2035 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 7.73 | 1.3 | 1 | 1 | 2713029.02 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 888 | Lighting Fixtures - Interior | D502002 | Interior Lighting | The interior lighting system consists of wall mounted and recessed CFL fixtures and recessed mounted fluorescent fixtures with T- 5 lamps, electronic ballasts, conduit and wire. About 25% of the fixtures are equipped with emergency power. | 2007 | 35 | 2042 | 2037 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 89297 | SF Building | 7.73 | 1.3 | 1 | 1 | 897345.55 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 831 | Non-Condensing Boilers | D302015 | Hot Water Boilers - Over 1000 MBH | Heating hot water is provided from two 8,000MBH, Cleaver Brooks, Model #: FL-700-8000-160HW, non-condensing, boilers. | 2012 | 30 | 2042 | 2042 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 16000 | MBH | 61.6 | 1.3 | 1 | 1 | 1281280 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 850 | Perimeter Heat System - Hydronic Fin Tube - 1998 | D305004 | Finned Tube Radiation Units | The HVAC distribution includes a two-pipe system of heating hot water with perimeter units. | 1998 | 30 | 2028 | 2028 | 2019-11-04 | 2 - Good | No significant deficiencies were observed. | 9000 | LF | 80.03 | 1.3 | 1 | 1 | 936351 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 861 | Precast Concrete Panel Exterior Walls | B201027 | Pre-Cast / Cast in Place Wall Panels | The exterior walls located on the 300 and 400 levels include sections of precast concrete panels. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | The precast concrete walls are in fair condition overall, no significant deficiencies were observed or reported. | 8826 | SF | 63.59 | 1.3 | 1 | 1 | 729618.94 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 841 | Roof and Floor Deck - Concrete Plank - Hollow Core | B101002 | Reinforced Concrete Floor | The building's roof deck is a concrete infilled metal pan deck on open web steel joists. | 1998 | 75 | 2073 | 2073 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed or reported. | 9049 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 906275.45 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 876 | Roof Deck - Metal Deck on Steel Frame | B102002 | Reinforced Concrete Roof | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1972 | 75 | 2047 | 2047 | 2019-11-04 | 1 - Excellent | The roof deck is in good condition overall; no significant deficiencies were observed or reported. | 11389 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 1140631.13 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 879 | Roof Deck - Metal Deck on Steel Frame | B102002 | Reinforced Concrete Roof | The roof deck is a concrete infilled metal pan deck on open web steel joists. | 1982 | 75 | 2057 | 2057 | 2019-11-04 | 1 - Excellent | The roof deck is in good condition overall. No significant deficiencies were observed or reported. | 9616 | SF Footprint | 77.04 | 1.3 | 1 | 1 | 963061.63 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 845 | Roof Drainage - Gravity | D204001 | Rain Water Drainage Piping and Fittings | Rain water drainage includes interior piping, roof drains and discharge piping by gravity flow to the municipal main. | 1998 | 50 | 2048 | 2048 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 2.65 | 1.3 | 1 | 1 | 930081.1 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 830 | Sanitary Waste | D203001 | Sanitary Waste and Vent Piping and Fittings | The building is provided with a sanitary waste system of cast iron piping with pumped discharge to the municipal system. | 2012 | 50 | 2062 | 2062 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175861 | SF Building | 4.15 | 1.3 | 1 | 1 | 948770.1 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 844 | Sanitary Waste - Gravity Discharge | D203001 | Sanitary Waste and Vent Piping and Fittings | The building includes an extensive sanitary waste system of cast iron, copper and PVC piping with gravity discharge to the municipal system. | 1998 | 50 | 2048 | 2048 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 4.15 | 1.3 | 1 | 1 | 1456542.1 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 828 | Sheet Flooring | C302006 | Masonry and Stone Floor | Resilient acid proof vinyl sheet flooring is provided in the chemistry labs. | 2012 | 50 | 2062 | 2027 | 2019-11-04 | 2 - Good | No significant deficiencies were observed or reported. | 20000 | SF | 51.36 | 1.3 | 1 | 1 | 1335360 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 885 | Solid Doors - Single | C102022 | Interior - Single Door - Wood | The buildings interior doors include hollow metal and wood doors with vision panels. | 2007 | 25 | 2032 | 2047 | 2019-11-04 | 1 - Excellent | The interior doors are in good condition overall, no major deficiencies were observed. | 238 | Each | 2527.14 | 1.3 | 1 | 1 | 781897.12 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 842 | Split face Masonry Unit Exterior Walls | B201021 | Masonry | The building's exterior wall system is a split face masonry unit exterior wall system. | 1998 | 75 | 2073 | 2073 | 2019-11-04 | 1 - Excellent | Efflorescence was observed in isolated areas, monitoring is recommended. | 12938 | SF | 52.22 | 1.3 | 1 | 1 | 878309.07 | 0 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 835 | Sprinklers | D401002 | Sprinklers | The building is equipped with a combined dry and wet sprinkler system with complete coverage throughout the building. The dry system reportedly protects the areas of loading dock, greenhouse, generator room, electrical rooms and the 426 Lounge. The wet system covers the rest of the building. | 2012 | 40 | 2052 | 2047 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 175861 | SF Building | 5.01 | 1.3 | 1 | 1 | 1145382.69 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 832 | Steam Boilers | D302003 | Fuel-Fired Forced Air Furnaces | The HVAC equipment includes two 150BHP, 6,276 MBH, Thermogenics Thermocoil Steam Boiler, Model #: MG 150 NAX, natural gas fired, steam boilers; one providing steam to six autoclaves; another providing humidification via a steam-to-steam generator. | 2012 | 18 | 2030 | 2042 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 12552 | MBH | 49.28 | 1.3 | 1 | 1 | 804131.33 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 825 | Stone Cladding | B201099 | Other Exterior Walls | The building&rsquo;s exterior finishes includes stone cladding exterior wall finish. | 2012 | 40 | 2052 | 2052 | 2019-11-04 | 1 - Excellent | The exterior wall finish is in good condition overall, no deficiencies were observed. | 550 | Lump Sum | 3850 | 1.3 | 1 | 1 | 2752750 | 1 | Active |  |  |  |  | Operations | Central
| 01.204 | 11 | Wilson Library | Cottage Grove | 852 | Wet Standpipe System | D402001 | Standpipes | The fire protection systems include a wet fire standpipe system with backflow protection, distribution piping and shutoff valves | 1998 | 40 | 2038 | 2033 | 2019-11-04 | 1 - Excellent | No significant deficiencies were observed. | 269980 | SF Building | 2.43 | 1.3 | 1 | 1 | 852866.82 | 1 | Active |  |  |  |  | Operations | Central